## Overview_data
GOLD_E_LonWorks_140611
FUNCTIONAL PROFILE:
GOLDen GATE Lonworks FTT-10, TBLZ-3-1-1-41, Version 1.00
GOLD RX/PX/CX/SD, GENERATION E
Applicable to program version 1.10 and newer versions
General
This document describes the profile at the GOLD-LON interface.
The LON interface is a separate communication unit that solely transfers data to and from the
control system in the GOLD air handling unit.
This edition of the GOLD-LON interface should be used for monitoring GOLD RX/PX/CX/SD
generation E, across a LON bus.
It is not possible to override the physical inputs of the GOLD air handling unit, only monitor
them across the LON bus.
The temperature and air flow set points can be adjusted across the LON network. The functions
in the GOLD control system can be adjusted, enabled or disabled. The integrated switching
clock can also be set to the current time.
The interface is normally equipped with a Transceiver for Twisted Pair Open Topology (TP/FT-10).
This is a ready-to-use module, developed and accepted by Echelon.
The LON software in the interface supports the self-documentation and Wink function and
thus helps with installing nodes across a network manager.
The network variables are to SNVT Standard.
The LON Interface can be illustrated as follow:
Figure 1
Functional profile
Power-Up State
All the input variables have a 0 reading before communication with the GOLD air handling unit
has been established.
When communication with the GOLD unit has been in progress for about 60 seconds, all the
input variables have been upgraded with the values from the GOLD air handling unit's internal
Flash.
This means that the input variables are always upgraded after a power failure and therefore
always indicate the current value, as long as the communication is OK:
LED/Keyed Functions
Normal operation:
The "Module Status" LED will flash green.
The "Serial Status" LED will flash green whenever acknowledged communication with the GOLD
takes place.
Service:
The "Service" LED will flash if the node has not been configured. Configuration is normally
carried out by a LON manager. While the LON manager is configuring the node, the operator
will be requested to depress "servicepin" to identify the node. The node has integrated self-
identification and self-description of the parameters.
Wink Function
This command can be used for identifying the GOLD air handling unit.
The "Serial Status" LEDs green and red flash alternately for 15 seconds while the Wink
command is being transmitted to the LON interface.
This input varable can be used for checking whether the LON network is intact up to the LON
interface and for identifying a specific air handling unit if several units are connected to the
same network.
LON-
Interface
Object
GOLD-
Air Handling Unit

## Funktional_profile
GOLD_E_LonWorks_140611
Figure 2
Functional profile number 8080
of LonMark Unit Ventilator object
details(variables not implemented
in GOLD are greyed).
nv1 nviSpaceTemp
SNVT_temp_p
nv21 nvoSpaceTemp
SNVT_temp_p
nv22 nvoEffectSetp
SNVT_temp_p
nv23 nvoUnitStatus
SNVT_hvac_status
nv2 nviSetpoint
SNVT_temp_p
nv3 nviSetptOffset
SNVT_temp_p
nv4 nviSetptShift
SNVT_temp_setpt
nv5 nviOccSchedule
SNVT_tod_event
nv6 nviOccManCmd
SNVT_occupancy
nv7 nviOccSensor
SNVT_occupancy
nv8 nviApplicMode
SNVT_hvac_mode
nv9 nviHeatCool
SNVT_hvac_Mode
nv10 nviFanSpeedCmd
SNVT_switch
nv11 nviComprEnable
SNVT_switch
nv12 nviAuxHeatEnable
SNVT_switch
nv13 nviEconEnable
SNVT_switch
nv14 nviEnergyHoldOff
SNVT_switch
nv15 nviValveOverride
SNVT_hvac_overid
nv16 nviEmergOverride
SNVT_hvac_emerg
nv17 nviSourceTemp
SNVT_temp_p
nv18 nviOutdoorTemp
SNVT_temp_p
nv19 nviSpaceRH
SNVT_lev_percent
nv20 nviOutdoorRH
SNVT_lev_percent
nv21 nviSpaceCO2
SNVT_ppm
nv24 nvoEffectOccup
SNVT_occupancy
nv25 nvoHeatCool
SNVT_hvac_mode
nv26 nvoSetpoint
SNVT_temp_p
nv27 nvoSetpShift
SNVT_temp_setp
nv28 nvoFanSpeed
SNVT_switch
nv29 nvoDischAirTemp
SNVT_temp_p
nv30 nvoLoadAbsK
SNVT_power_kilo
nv31 nvoTerminalLoad
SNVT_lev_percent
nv35 nvoOADamper
SNVT_lev_percent
nv36 nvoSpaceRH
SNVT_lev_percent
nv37 nvoOutdoorRh
SNVT_lev_percent
nv32 nvoHeatPrimary
SNVT_lev.percent
nv33 nvoHeatSecondary
SNVT_lev_percent
nv34 nvoCoolPrimary
SNVT_lev_percent
nv38 nvoOutdoorTemp
SNVT_temp_p
nv39 nvoSpaceCO2
SNVT_ppm
nv40 nvoEnergyHoldOff
SNVT_switch
Unit Ventilator
Controler number 8080
Mandatory
Network
Variables
Optional
Network
Variables
Manufacturer
Defined
Section
See following pages
See following pages
nc49 Send Heartbeat
nc60 Occupancy Temperature Setpoints
nc52 Minimum Send Time
nc48 Receive Hartbeat
nc17 Location Label
nc34 Local Bypass Time
nc35 Manual Override Time
nc23 Outdoor Air Damper Minimum Position
nc42 Space CO2 Limit
nc36 Space Humidity Setpoint
nc59 Number of Heating/Cooling Valves
(mandatory)
(mandatory)
(optional)
(optional)
(optional)
(optional)
(optional)
(optional)
(optional)
(optional)
(optional)
Configuration Properties
Hardware
Input
Hardware
Output

## Overview_parameters
GOLD_E_LonWorks_140611
Extract air filter pressure level |  | nvoEA_filterLev | EA Duct pressure |  | nvoEF_pressure | EA/Room temperature |  | nvoEAtemp
EA filter pressure level limit |  | nvoEA_filteralr | EA Low speed pressure setpoint |  | nviEF_LSpressure | EA/Room temperature setpoint |  | nviEAtempset
|  |  | EA High speed pressure setpoint |  | nviEF_HSpressure | SA Min temperature setpoint |  | nviMinSAtemp
[6 empty] | SA Max temperature setpoint |  | nviMaxSAtemp
Operation level | nvoOperationLev
Communication | nviComOperation
operation level | [5 empty] | SA Duct pressure |  | nvoSF_pressure
Operation active | nvoOP_relay |  |  |  |  | SA Low speed pressure point |  | nviSF_LSpressure
Low speed active | nvoLS_relay |  |  |  |  | SA High speed pressure point |  | nviSF_HSpressure
High speed active | nvoHS_relay
Damper active | nvoDamper_relay
Triggered alarm #1 | nvoTriggAlarm1
A-alarm active | nvoA_alarm_relay
B-alarm active | nvoB_alarm_relay
Alarm reset | nviAlarm_reset |  |  |  |  | SA Temperature |  | nvoSAtemp
[6 empty] | SA Temperature setpoint |  | nviSetpoint
[6 empty] | ERS 1 Diff |  | nviERS1diff
EA Airflow | nvoEF_flow
EA Fan level | nvoEF_speed
EA Low speed | nviEF_LSflow
airflow setpoint
EA High speed | nviEF_HSflow
airflow setpoint | [5 empty] | Cooling level |  | nvoCoolPrimary
[6 empty] | Cool output 1 |  | nvoCool_1_relay
Outdoor temperature | nvoOUTtemp |  |  |  |  | Cool output 2 |  | nvoCool_2_relay
Supply air filter pressure level |  | nvoSA_filterLev
SA filter pressure level limit |  | nvoSA_filteralr
|  |  | SA Airflow | nvoSF_flow |  | Reheat level |  | nvoHeatSecondary
Heat exchange regulator |  | nvoHeatPrimaryRe | SA Fan level | nvoFanSpeed |  | Heat output |  | nvoHeat_relay
|  |  | SA Low speed airflow setpoint | nviSF_LSflow |  | Anti frost temperature |  | nvoFrosttemp
|  |  | SA High speed airflow setpoint | nviSF_HSflow

## SNVT
GOLD_E_LonWorks_140611
NV Index | SNVT No | SNVT Name | SNVT Type | Description | Min | Max | Unit | Default | Misc
Alarm settings
0 | 100 | nviAlarm_reset | SNVT_switch | Alarm Reset Act Resets all active alarms | 0 | 1 |  | 0
1 | 101 | nvoAlarm_reset |  | Alarm Reset
2 | 104 | nviInt_fire_func | SNVT_switch | Int Fire Al Act | 0 | 1 |  | 0
3 | 105 | nvoInt_fire_func |  | Int Fire Al
4 | 106 | nviInt_fire_ReFu | SNVT_switch | Int Fire Al Res Func Act 0=manual reset, 1=auto reset | 0 | 1 |  | 0
5 | 107 | nvoInt_fire_ReFu |  | Int Fire Al Res Func
6 | 112 | nviExt_fire1_ReF | SNVT_switch | Ext Fire Al1 Res Func Act 0=manual reset, 1=auto reset | 0 | 1 |  | 0
7 | 113 | nvoExt_fire1_ReF |  | Ext Fire Al1 Res Func
8 | 114 | nviExt_fire2_ReF | SNVT_switch | Ext Fire Al2 Res Func Act 0=manual reset, 1=auto reset | 0 | 1 |  | 0
9 | 115 | nvoExt_fire2_ReF |  | Ext Fire Al2 Res Func
10 | 120 | nviExt_Alr1_ReFu | SNVT_switch | Ext Al1 Res Func Act 0=manual reset, 1=auto reset | 0 | 1 |  | 0
11 | 121 | nvoExt_Alr1_ReFu |  | Ext Al1 Res Func
12 | 122 | nviExt_Alr2_ReFu | SNVT_switch | Ext Al2 Res Func Act 0=manual reset, 1=auto reset | 0 | 1 |  | 0
13 | 123 | nvoExt_Alr2_ReFu |  | Ext Al2 Res Func
14 | 128 | nviExt_alr1_func | SNVT_switch | Ext Al1 Cond Func Act 0=alarm at closed contact, 1=alarm at open contact | 0 | 1 |  | 0
15 | 129 | nvoExt_alr1_func |  | Ext Al1 Cond Func
16 | 130 | nviExt_alr2_func | SNVT_switch | Ext Al2 Cond Func Act 0=alarm at closed contact, 1=alarm at open contact | 0 | 1 |  | 0
17 | 131 | nvoExt_alr2_func |  | Ext Al2 Cond Func
Operation level/alarm
18 | 200 | nvoOP_relay | SNVT_switch | Operating Relay output status | 0 | 1
19 | 201 | nvoDamper_relay | SNVT_switch | Damper Relay output status | 0 | 1
20 | 202 | nvoLS_relay | SNVT_switch | Low Spd Low speed operation status | 0 | 1
21 | 203 | nvoHS_relay | SNVT_switch | High Spd High speed operation status | 0 | 1
22 | 204 | nvoNH_active | SNVT_switch | Int nightheat | 0 | 1
23 | 205 | nvoMB_active | SNVT_switch | Morning bst | 0 | 1
24 | 206 | nvoHB_active | SNVT_switch | Heat bst | 0 | 1
25 | 207 | nvoCB_active | SNVT_switch | Cooling boost | 0 | 1
26 | 208 | nvoNC_active | SNVT_switch | Smrnight Cool | 0 | 1
27 | 212 | nvoA_alarm_relay | SNVT_switch | Alrm A Any alarm with priority class A active | 0 | 1
28 | 213 | nvoB_alarm_relay | SNVT_switch | Alrm B Any alarm with priority class B active | 0 | 1
Heat exchange
29 | 216 | nvoHX_active | SNVT_switch | HX op active HX status | 0 | 1
30 | 217 | nvoHX_recovery | SNVT_switch | HX recovery active HX cool recovery status | 0 | 1
31 | 218 | nvoHX_defrost | SNVT_switch | HX defrost active HX defrost status | 0 | 1
32 | 221 | nvoRHX_rotation | SNVT_switch | R.HX. Rotation Monitor RHX speed monitor status | 0 | 1
33 | 226 | nvoCHX_relay | SNVT_switch | C.HX. Pump output Relay output status | 0 | 1
AHU Coils
34 | 232 | nvoExtRegSeqRe | SNVT_switch | Extra reg seq output Relay output status | 0 | 1
35 | 237 | nvoHeat_relay | SNVT_switch | Pmp Heat Relay output status | 0 | 1
36 | 242 | nvoCool_1_relay | SNVT_switch | Cool 1 Relay output status | 0 | 1
37 | 243 | nvoCool_2_relay | SNVT_switch | Cool 2 Relay output status | 0 | 1
Pre-heat
38 | 250 | nvoPreHeat_relay | SNVT_switch | Pre-heat output Relay output status | 0 | 1
Xzone
39 | 255 | nvoXzone_heat_re | SNVT_switch | Xzone heat output Relay output status | 0 | 1
40 | 262 | nvoXzone_cool_r1 | SNVT_switch | Xzone cool output 1 Relay output status | 0 | 1
41 | 263 | nvoXzone_cool_r2 | SNVT_switch | Xzone cool output 2 Relay output status | 0 | 1
AYC
42 | 298 | nvoAYC_HeatPmpRe | SNVT_switch | AYC heat pmp output Relay output status | 0 | 1
43 | 303 | nvoAYC_CoolPmpRe | SNVT_switch | AYC cool pmp output Relay output status | 0 | 1
COOL DX
44 | 308 | nvoCoolDX1_relay | SNVT_switch | Cool DX 1 Relay output status | 0 | 1
45 | 314 | nvoCoolDX2_relay | SNVT_switch | Cool DX 2 Relay output status | 0 | 1
Alarms
46 | 399 | nvoAlarmOut | SNVT_alarm | Location = "GOLD". Object ID = Alarm number (0-1500). Alarm type = Contains either no alarm or an unspecified alarm. Priority level = alarm priority (No comm.=7, A=1, B=2, Info=3 and none=0). Index to SNVT = Not used. Always set at 0. Value = Not used Always set at 0. Year, month, day = Date when alarm tripped. Alarm limit = Not used. Always set at 0.
AHU Air flow/duct pressure
47 | 401 | nvoAHU_type | SNVT_count | AHU type 10=GOLD RX, 11=GOLD PX, 12=GOLD CX, 13=GOLD SD/SA,14=GOLD SD/EA, 15=GOLD SD/SA+CX, 16=GOLD SD/SA+EA, 17=GOLD SD/SA+EA+CX | 0 | 999
48 | 402 | nvoAirFlowDir | SNVT_switch | Air flow direction 0=Fan no.2 as SA, 1=Fan no.1 as SA. | 0 | 1
Air flow regulation
49 | 403 | nvoSF_flow | SNVT_flow | Sup AF Present supply air flow. | 0 | 20000 | l/s
50 | 404 | nvoSF_flowreg | SNVT_flow | Sup AF reg Present supply air flow regulator set point. | 0 | 20000 | l/s
51 | 405 | nvoEF_flow | SNVT_flow | Ext AF Present extract air flow. | 0 | 20000 | l/s
52 | 406 | nvoEF_flowreg | SNVT_flow | Ext AF reg Present extract air flow regulator set point. | 0 | 20000 | l/s
Pressure regulation
53 | 407 | nvoSF_pressure | SNVT_press_p | Sup air duct pres Present supply air duct pressure. | 0.0 | 2000.0 | Pa
54 | 408 | nvoSF_press_reg | SNVT_press_p | Sup air duct pres reg Present supply air duct pressure regulator set point. | 0.0 | 2000.0 | Pa
55 | 409 | nvoEF_pressure | SNVT_press_p | Ext air duct pres Present extract air duct pressure. | 0.0 | 2000.0 | Pa
56 | 410 | nvoEF_press_reg | SNVT_press_p | Ext air duct pres reg Present extract air duct pressure regulator set point. | 0.0 | 2000.0 | Pa
Demand regulation
57 | 411 | nvoDemand_lev | SNVT_lev_percent | In sig air VAV dmnd Present input signal for demand regulation. | 0.00 | 100.00 | %
58 | 412 | nvoDemand_reg | SNVT_lev_percent | VAV dmnd regulator Present demand regulator set point. | 0.00 | 100.00 | %
Air flow pressure sensors
59 | 413 | nvoSF_fan_press | SNVT_press_p | Sup air pres Present air flow pressure in the supply air fan inlet. | 0.0 | 2000.0 | Pa
60 | 414 | nvoEF_fan_press | SNVT_press_p | Ext air pres Present air flow pressure in the extract air fan inlet. | 0.0 | 2000.0 | Pa
Filters
61 | 422 | nvoSA_PfilterLev | SNVT_press_p | Sup air preflt prs drop Present supply air pre-filter pressure drop. | 0.0 | 2000.0 | Pa
62 | 423 | nvoSA_Pfilteralr | SNVT_press_p | Sup air preflt prs drop alrm lev Present supply air pre-filter pressure alarm limit. | 0.0 | 2000.0 | Pa
63 | 424 | nvoEA_PfilterLev | SNVT_press_p | Ext air preflt prs drop Present extract air pre-filter pressure drop. | 0.0 | 2000.0 | Pa
64 | 425 | nvoEA_Pfilteralr | SNVT_press_p | Ext air preflt prs drop alrm lev Present extract air pre-filter pressure alarm limit. | 0.0 | 2000.0 | Pa
65 | 426 | nvoSA_filterLev | SNVT_press_p | Sup air flt prs drop Present supply air filter pressure drop. | 0.0 | 2000.0 | Pa
66 | 427 | nvoSA_filteralr | SNVT_press_p | Sup air flt prs drop alrm lev Present supply air filter pressure alarm limit. | 0.0 | 2000.0 | Pa
67 | 428 | nvoEA_filterLev | SNVT_press_p | Ext air flt prs drop Present extract air filter pressure drop. | 0.0 | 2000.0 | Pa
68 | 429 | nvoEA_filteralr | SNVT_press_p | Ext air flt prs drop alrm lev Present extract air filter pressure alarm limit. | 0.0 | 2000.0 | Pa
69 | 430 | nvoSA_EfilterLev | SNVT_press_p | Sup air endflt prs drop Present supply air end-filter pressure drop. | 0.0 | 2000.0 | Pa
70 | 431 | nvoSA_Efilteralr | SNVT_press_p | Sup air endflt prs drop alrm lev Present supply air end-filter pressure alarm limit. | 0.0 | 2000.0 | Pa
Fans
71 | 28 | nvoFanSpeed | SNVT_switch | Fan Speed Output Present fan speed level of the supply air fan. | 0.00 | 100.00 | %
72 | 437 | nvoEF_speed | SNVT_switch | Run lvl ext air fan Present fan speed level of the extract air fan. | 0.00 | 100.00 | %
73 | 438 | nvoSF_rpm | SNVT_count | Sup air fan rpm Present fan speed level of the supply air fan. | 0 | 4000 | rpm
74 | 439 | nvoEF_rpm | SNVT_count | Ext air fan rpm Present fan speed level of the extract air fan. | 0 | 4000 | rpm
75 | 440 | nvoSF_voltage | SNVT_volt | Volt sup air fan Present voltage level of the supply air fan. | 0 | 500 | V
76 | 441 | nvoEF_voltage | SNVT_volt | Volt ext air fan Present voltage level of the extract air fan. | 0 | 500 | V
77 | 442 | nvoSF_current | SNVT_amp | Current sup air fan Present current level of the supply air fans. Includes all supply air fans. | 0 | 32.700 | A
78 | 443 | nvoEF_current | SNVT_amp | Current ext air fan Present current level of the extract air fans. Includes all supply air fans. | 0 | 32.700 | A
79 | 444 | nvoSF_power | SNVT_count | Consm lev for sup air fan Present power level of the supply air fans. Includes all supply air fans. | 0 | 45.0 | kW
80 | 445 | nvoEF_power | SNVT_count | Consm lev for ext air fan Present power consumption level of the extract air fans. Includes all extract air fans. | 0 | 45.0 | kW
81 | 446 | nvoSF_KWh | SNVT_count | KWh for sup air fan Total power consumption of the supply air fans. Includes all supply air fans. | 0 | 9999 | kWh
82 | 447 | nvoEF_KWh | SNVT_count | KWh for ext air fan Total power consumption level of the extract air fans. Includes all extract air fans. | 0 | 9999 | kWh
83 | 448 | nvoSF_MWh | SNVT_count | MWh for sup air fan Total power consumption of the supply air fans. Includes all supply air fans. | 0 | 9999 | MWh
84 | 449 | nvoEF_MWh | SNVT_count | MWh for ext air fan Total power consumption level of the extract air fans. Includes all extract air fans. | 0 | 9999 | MWh
85 | 450 | nvoSF_Optime | SNVT_count | Sup air fan op time days Total operation time of the supply air fan presented in days (24h). | 0..9999 | 9999 | days
86 | 451 | nvoEF_Optime | SNVT_count | Ext air fan op time days Total operation time of the extract air fan presented in days (24h). | 0..9999 | 9999 | days
87 | 454 | nvoSF_flow_min | SNVT_flow | Sup AF min Supply air AHU min air flow | 0 | 18000 | l/s
88 | 455 | nvoEF_flow_min | SNVT_flow | Ext AF min Extract air AHU min air flow | 0 | 18000 | l/s
89 | 456 | nvoSF_flow_max | SNVT_flow | Sup AF max Supply air AHU max air flow | 0 | 18000 | l/s
90 | 457 | nvoEF_flow_max | SNVT_flow | Ext AF max Extract air AHU max air flow | 0 | 18000 | l/s
91 | 462 | nvoSFP | SNVT_lev_percent | SFP Calculated SFP level. | 0.0 | 1000.0 | kW/m3/s
AHU Temperature sensors
92 | 463 | nvoSAtemp | SNVT_temp_p | Sup air temp Present supply air temperature. | -55.00 | 125.00 | °C
93 | 464 | nvoSA_D_temp | SNVT_temp_p | Supply air-D temp Present supply air density temperature. | -55.00 | 125.00 | °C
94 | 465 | nvoEAtemp | SNVT_temp_p | Ext air/room temp in unit Present extract air temperature in the unit. | -55.00 | 125.00 | °C
95 | 466 | nvoEA_D_temp | SNVT_temp_p | Extract air-D temp Present extract air density temperature. | -55.00 | 125.00 | °C
96 | 467 | nvoEAreg_temp | SNVT_temp_p | Ext air/room temp used for reg Present extract air temperature used for regulation. | -55.00 | 125.00 | °C
97 | 472 | nvoOUTtemp | SNVT_temp_p | Outd air temp in unit Present outdoor air temperature in the unit. | -55.00 | 125.00 | °C
98 | 473 | nvoOUTreg_temp | SNVT_temp_p | Outd air temp used for reg Present outdoor air temperature used for regulation. | -55.00 | 125.00 | °C
99 | 38 | nvoOutdoorTemp | SNVT_temp_p | Outdoor Air Temperature Output Present calculated min, max or average (depending of configuration) temperature of outd. sensor 1-4. | -55.00 | 125.00 | °C
100 | 1 | nviSpaceTemp | SNVT_temp_p | Space Temperature Input Present calculated min, max or average (depending of configuration) temperature of room sensor 1-4. nviSpaceTemp Not used in present SW version. Se also nviRoomTempBMS NV index 392. | -55.00 | 125.00 | °C
101 | 21 | nvoSpaceTemp | SNVT_temp_p | Space Temperature Input
AHU Temperature regulation
102 | 22 | nvoEffectSetpt | SNVT_temp_p | Effective Setpoint Output (sup air) Present supply air temperature regulator set point. | 0.00 | 50.00 | °C
103 | 487 | nvoEAtempset_reg | SNVT_temp_p | Ext air temp regulator Present extract air temperature regulator set point. | 0.00 | 50.00 | °C
104 | 490 | nvoHeatPrimaryRe | SNVT_lev_percent | Heat exchange reg Present operation level of the rotary heat exchanger. | 0.00 | 100.00 | %
105 | 491 | nvoEXreg_Heat | SNVT_lev_percent | Lev extra reg seq heat Present level of extra regulation heat. | 0.00 | 100.00 | %
106 | 33 | nvoHeatSecondary | SNVT_lev_percent | Sec Heat Output Present level of reheat. | 0.00 | 100.00 | %
107 | 495 | nvoReCO2_Heat | SNVT_lev_percent | ReCO2 heat level Present level of ReCO2 heat. | 0.00 | 100.00 | %
108 | 496 | nvoFanDownReg | SNVT_lev_percent | Lev fan air down reg Present level of fan down regulation. | 0.00 | 100.00 | %
109 | 497 | nvoHeatboost | SNVT_lev_percent | Lev heat boost Present level of heating boost. | 0.00 | 100.00 | %
110 | 498 | nvoEXreg_Cool | SNVT_lev_percent | Lev extra reg seq cool Present level of extra regulation cool. | 0.00 | 100.00 | %
111 | 34 | nvoCoolPrimary | SNVT_lev_percent | Primary Cool Output Present level of cooling. | 0.00 | 100.00 | %
112 | 502 | nvoReCO2_Cool | SNVT_lev_percent | ReCO2 cool level Present level of ReCO2 heat. | 0.00 | 100.00 | %
113 | 503 | nvoCoolboost | SNVT_lev_percent | Lev cool boost Present level of cooling boost. | 0.00 | 100.00 | %
AHU heat exchange
114 | 32 | nvoHeatPrimary | SNVT_lev_percent | Prim Heat Output Present speed level of the rotary heat exchanger. | 0.00 | 100.00 | %
115 | 505 | nvoRHX_eff | SNVT_lev_percent | R.HX Efficiency Calculated level of rotary heat exchanger efficiency. | 0.00 | 100.00 | %
116 | 506 | nvoHX_pressure | SNVT_press_p | Press drop rot heat exchr Present pressure drop for the rotary heat exchanger. | 0.0 | 2000.0 | Pa
117 | 507 | nvoHX_pressalr | SNVT_press_p | Press drop alarm lmt rot heat exchr Present pressure drop alarm limit for the rotary heat exchanger. | 0.0 | 2000.0 | Pa
118 | 506 | nvoHX_PurgPress | SNVT_press_p | Press drop rot heat exchr purg Present pressure difference for the rotary heat exchangers purging sector. | 0.0 | 1000.0 | Pa
119 | 510 | nvoHX_Optime | SNVT_count | Heat X op time days Total operation time of the rotary heat exchanger presented in days (24h). | 0 | 9999 | Days
120 | 516 | nvoPHX_bypass_op | SNVT_lev_percent | P.HX bypass output Present level of plate heat exchanger bypass output. | 0.00 | 100.00 | %
121 | 518 | nvoPHX_temp_1 | SNVT_temp_p | P.HX Temp 1 Present bypass temperature sensor 1 in plate heat exchanger. | -55.00 | 125.00 | °C
122 | 519 | nvoPHX_temp_2 | SNVT_temp_p | P.HX Temp 2 Present bypass temperature sensor 2 in plate heat exchanger. | -55.00 | 125.00 | °C
123 | 526 | nvoCHX_valve_op | SNVT_lev_percent | C.HX Valve output Present level of coil heat exchanger valve output. | 0.00 | 100.00 | %
124 | 528 | nvoCHX_temp | SNVT_temp_p | C.HX Temp Present return water temperature for coil heat exchanger. | -55.00 | 125.00 | °C
125 | 529 | nvoPCHX_Optime | SNVT_count | P/C.HX op time days Total operation time of the coil heat exchanger presented in days (24h). | 0 | 9999 | Days
126 | 535 | nvoPCHX_humidity | SNVT_lev_percent | P/C.HX Humidity Present level of air-humidity for calculation of bypass/valve limitation. | 0.00 | 100.00 | %
AHU Coils
127 | 552 | nvoEXregFrostT | SNVT_temp_p | Extra reg seq anti frost temp Present extra regulation anti frost temperature for water heat coil. Value 0=overheat when electric heat is used. | -55.00 | 125.00 | °C
128 | 552 | nvoFrosttemp | SNVT_temp_p | Anti frost temp Present anti frost temperature for water heat coil. Value 0=overheat when electric heat is used. | -55.00 | 125.00 | °C
129 | 558 | nvoHeat_Optime | SNVT_count | Reheat op time days Total operation time of re-heat presented in days (24h). | 0 | 9999 | Days
130 | 563 | nvoCoolCoilTemp | SNVT_temp_p | Cool coil water temp Present cool water temperature for water cool coil. | -55.00 | 125.00 | °C
131 | 568 | nvoCool_Optime | SNVT_count | Cooling op time days Total operation time of cool presented in days (24h). | 0 | 9999 | Days
Xzone temperature sensors
132 | 573 | nvoXzone_SA_temp | SNVT_temp_p | Xzone SA temp Present supply air temperature. | -55.00 | 125.00 | °C
133 | 574 | nvoXzone_EA_temp | SNVT_temp_p | Xzone EA temp Present extract air temperature in the unit. | -55.00 | 125.00 | °C
134 | 575 | nvoXZ_RoomEAtemp | SNVT_temp_p | Xzone EA/Room temp Present extract air temperature used for regulation. | -55.00 | 125.00 | °C
135 | 580 | nvoXZ_Room_temp | SNVT_temp_p | Xzone Room temp min/max/av Present calculated min, max or average (depending on configuration) temperature of room sensor 1-4. | -55.00 | 125.00 | °C
Xzone Temperature regulation
136 | 585 | nvoXZ_SAtemp_reg | SNVT_temp_p | Xzone SA temp reg Present supply air temperature regulator set point. | 0.00 | 50.00 | °C
137 | 586 | nvoXZ_EAtemp_reg | SNVT_temp_p | Xzone EA temp reg Present extract air temperature regulator set point. | 0.00 | 50.00 | °C
138 | 589 | nvoXzoneHeatSec | SNVT_lev_percent | Xzone Sec Heat Output | 0.00 | 100.00 | %
139 | 592 | nvoXzoneCoolPrim | SNVT_lev_percent | Xzone Primary Cool Output | 0.00 | 100.00 | %
Xzone coils
140 | 598 | nvoXzoneFrosttem | SNVT_temp_p | Xzone Primary Cool Output Present Xzone heat anti frost temperature for water heat coil. Value 0=Overheat when electric heat is used. | -55.00 | 125.00 | °C
141 | 609 | nvoXZ_CoolCoil_T | SNVT_temp_p | Xzone Cool coil water temp | -55.00 | 125.00 | °C
Pre-heat
142 | 619 | nvoPreHeat_temp | SNVT_temp_p | Pre-heat air temp Present pre-heat temperature. | -55.00 | 125.00 | °C
143 | 619 | nvoPH_temp_reg | SNVT_temp_p | Pre-heat air temp reg Present pre-heat temperature regulator set point. | -40.00 | 40.00 | °C
144 | 621 | nvoPreHeat_level | SNVT_lev_percent | Pre-heat level
145 | 624 | nvoPreHeatFrostT | SNVT_temp_p | Pre-heat anti frost temp Present pre-heat anti frost temperature for water heat coil. Value 0=Overheat when electric heat is used. | -55.00 | 125.00 | °C
ReCO2
146 | 632 | nvoReCO2_IntDamp | SNVT_lev_percent | ReCO2 internal damper output Present output signal to the recirculation damper. | 0.00 | 100.00 | %
147 | 634 | nvoReCO2_ExtDamp | SNVT_lev_percent | ReCO2 external damper output Present output signal to the outdoor air damper. | 0.00 | 100.00 | %
148 | 636 | nvoReCO2_OutAirF | SNVT_flow | ReCO2 outdoor airflow Present outdoor air flow level. | 0.0 | NV 89 | l/s
149 | 637 | nvoReCO2_OAF_reg | SNVT_flow | ReCO2 outdoor airflow reg Present outdoor air flow regulator set point. | 0.0 | NV 89 | l/s
Humidity
150 | 643 | nvoSA_humidity | SNVT_lev_percent | Supply air-humidity Present level of supply air humidity | 0.00 | 100.00 | %RH
151 | 644 | nvoSA_humidity_t | SNVT_temp_p | Supply air-humidity temp Present temperature inside the supply air humidity sensor. | -40.00 | 123.00 | °C
152 | 645 | nvoSA_dewpoint | SNVT_temp_p | Supply air-dewpoint Calculated supply air dew point. | -40.00 | 40.00 | °C
153 | 646 | nvoEA_humidity | SNVT_lev_percent | Extract air-humidity Present level of extract air humidity. | 0.00 | 100.00 | %RH
154 | 647 | nvoEA_humidity_t | SNVT_temp_p | Extract air-humidity temp Present temperature inside the extract air humidity sensor. | -40.00 | 123.00 | °C
155 | 648 | nvoEA_dewpoint | SNVT_temp_p | Extract air-dewpoint Calculated extract air dew point. | -40.00 | 40.00 | °C
156 | 650 | nvoSA_dewpoint_r | SNVT_temp_p | Supply air-dewpoint reg Present supply air dew point regulator point. | -40.00 | 40.00 | °C
157 | 651 | nvoDehum_level | SNVT_lev_percent | Dehumidifying output level Present level of the dehumidifying output. | 0.00 | 100.00 | %
158 | 653 | nvoSA_humidi_r | SNVT_temp_p | Supply air-humidifying reg | 0.00 | 100.00 | %RH
159 | 654 | nvoHumidi_level | SNVT_lev_percent | Humidifying output level Present level of the humidifying output. | 0.00 | 100.00 | %
VOC
160 | 665 | nvoVOC_level | SNVT_count | VOC level Present level of VOC | 450 | 10000 | ppm
SMART Link
161 | 692 | nvoSL_WB_WaterA | SNVT_temp_p | SL WB outlet water average | -40.0 | 176.0 | °C
162 | 693 | nvoSL_WB_ReturnW | SNVT_temp_p | SL WB return water | -40.0 | 176.0 | °C
163 | 696 | nvoSL_WB_HeatedW | SNVT_temp_p | SL WB heated water | -40.0 | 176.0 | °C
164 | 697 | nvoSL_WB_CoolW | SNVT_temp_p | SL WB chilled water | -40.0 | 176.0 | °C
165 | 718 | nvoSL_WB_active | SNVT_switch | SL WB operation
166 | 719 | nvoSL_WB_CoolM | SNVT_switch | SL WB cool mode
167 | 722 | nvoSL_DX1_active | SNVT_switch | SL DX1 operation | 0 | 1
168 | 723 | nvoSL_DX1_CoolM | SNVT_switch | SL DX1 cool mode | 0 | 1
169 | 726 | nvoSL_DX1_PowerS | SNVT_lev_percent | SL DX1 power level set | 0 | 100.00 | %
170 | 733 | nvoSL_DX2_active | SNVT_switch | SL DX2 operation | 0 | 1
171 | 734 | nvoSL_DX2_CoolM | SNVT_switch | SL DX2 cool mode | 0 | 1
172 | 737 | nvoSL_DX2_PowerS | SNVT_lev_percent | SL DX2 power level set | 0 | 100.00 | %
173 | 744 | nvoSL_DX3_active | SNVT_switch | SL DX3 operation | 0 | 1
174 | 745 | nvoSL_DX3_CoolM | SNVT_switch | SL DX3 cool mode | 0 | 1
175 | 748 | nvoSL_DX3_PowerS | SNVT_lev_percent | SL DX3 power level set | 0 | 100.00 | %
176 | 755 | nvoSL_DX4_active | SNVT_switch | SL DX4 operation | 0 | 1
177 | 756 | nvoSL_DX4_CoolM | SNVT_switch | SL DX4 cool mode | 0 | 1
178 | 759 | nvoSL_DX4_PowerS | SNVT_lev_percent | SL DX4 power level set | 0 | 100.00 | %
AYC
179 | 773 | nvoAYC_Heat_temp | SNVT_temp_p | AYC heat temp Present heat temperature. | -55.00 | 125.00 | °C
180 | 774 | nvoAYC_Heat_reg | SNVT_temp_p | AYC heat temp reg Present heat temperature regulator set point. | -55.00 | 125.00 | °C
181 | 775 | nvoAYC_HeatValve | SNVT_lev_percent | AYC heat valve output Present level of the heat valve output. | 0 | 100.00 | %
182 | 778 | nvoAYC_HeatDeman | SNVT_lev_percent | AYC heat demand | 0 | 100.00 | % |  | 1.10
183 | 786 | nvoAYC_Cool_Tmp | SNVT_temp_p | AYC cool temp Present cool temperature. | -55.00 | 125.00 | °C
184 | 787 | nvoAYC_Cool_Reg | SNVT_temp_p | AYC cool temp reg Present cool temperature regulator set point. | -55.00 | 125.00 | °C
185 | 788 | nvoAYC_CoolValve | SNVT_lev_percent | AYC cool valve output Present cool of the heat valve output. | 0 | 100.00 | %
186 | 791 | nvoAYC_CoolDeman | SNVT_lev_percent | AYC cool demand | 0 | 100.00 | % |  | 1.10
Software
187 | 969 | nvoIQlogicVer | SNVT_count | IQlogic software ver Present controller software version | 0.00 | 99.00
Operation level
188 | 991 | nvoOperationLev | SNVT_count | Operation level 0=Fan not available 1=Alarm stop 2=Manual total stop (on hand terminal) 3=External total stop (digital input) 4=Communication total stop 5=Communication normal stop 6=Communication extended normal stop 7=Time channel total stop 8=Time channel normal stop 9=Time channel extended normal stop 10=Low speed=normal stop 11=SA Fan starting up 12=Fan regulation blocked 13=ReCO2 100% recirculation 14=Morning boost stop 15=Intermittent night heat stop 16=After cooling electric heater 17=COOL DX switch off delay 18=Damper switch off delay 19=Manual low speed (on hand terminal) 20=External low speed (digital input) 21=Extended external low speed 22=Communication low speed 23=Time channel low speed 24=Morning boost low speed 25=Intermittent night heat low speed 26=Manual high speed (on hand terminal) 27=External high speed (digital input) 28=Extended external high speed 29=Communication high speed 30=Time channel high speed 31=Summer night cooling high speed 32=Filter calibration 33=RHX Defrost calibration 34=ReCO2 calibration 35=AHU start up 36=Re-heat ramp down 37=HX ramp down 38=Air adjustment 39=Fans in operation with active fire alarm | 0 | 100
Alarms
189 | 1003 | nvoTriggAlarm1 | SNVT_count | Triggered alarm1 ((Alarm group - 1) x 15) + alarm number in group=Triggered alarm number. Zero if no triggered alarm. | 0 | 1500
190 | 1004 | nvoTriggAlarm2 | SNVT_count | Triggered alarm2 | 0 | 1500
191 | 1005 | nvoTriggAlarm3 | SNVT_count | Triggered alarm3 | 0 | 1500
192 | 1006 | nvoTriggAlarm4 | SNVT_count | Triggered alarm4 | 0 | 1500
193 | 1007 | nvoTriggAlarm5 | SNVT_count | Triggered alarm5 | 0 | 1500
194 | 1008 | nvoTriggAlarm6 | SNVT_count | Triggered alarm6 | 0 | 1500
195 | 1009 | nvoTriggAlarm7 | SNVT_count | Triggered alarm7 | 0 | 1500
196 | 1010 | nvoTriggAlarm8 | SNVT_count | Triggered alarm8 | 0 | 1500
197 | 1011 | nvoTriggAlarm9 | SNVT_count | Triggered alarm9 | 0 | 1500
198 | 1012 | nvoTriggAlarm10 | SNVT_count | Triggered alarm10 | 0 | 1500
Time schedule
199 | 1054 | nvoCurrentAction | SNVT_count | Time schedule action 1=Total stop, 2=Low speed, 3=High speed, 4=Normal stop, 5=Extended normal stop | 1 | 5
200 | 1056 | nvoException1_A | SNVT_switch | Exception 1 active 0=Inactive, 1=Active | 0 | 1
201 | 1057 | nvoException2_A | SNVT_switch | Exception 2 active 0=Inactive, 1=Active | 0 | 1
202 | 1058 | nvoCalendar1_A | SNVT_switch | Calendar 1 active 0=Inactive, 1=Active | 0 | 1
203 | 1059 | nvoCalendar2_A | SNVT_switch | Calendar 2 active 0=Inactive, 1=Active | 0 | 1
AHU fan regulation
204 | 1100 | nviSFregmode | SNVT_count | SA Fan reg mode Setting of regulation type for the supply air fan. 0=Air flow reg. 1=Pressure reg. 2=Demand reg. 3=Slave controlled by EA fan | 0 | 3 |  | 0
205 | 1101 | nvoSFregmode | SNVT_count | SA Fan reg mode
206 | 1102 | nviEFregmode | SNVT_count | EA Fan reg mode Setting of regulation type for the extract air fan. 0=Air flow reg. 1=Pressure reg. 2=Demand reg. 3=Slave controlled by SA fan | 0 | 3 |  | 0
207 | 1103 | nvoEFregmode | SNVT_count | EA Fan reg mode
Air flow regulation
208 | 1104 | nviSF_LSflow | SNVT_flow | Sup air flow lw spd Supply air flow set point for the unit when running in low speed operation. | 0 | NV 213 | l/s
209 | 1105 | nvoSF_LSflow | SNVT_flow | Sup air flow lw spd
210 | 1106 | nviEF_LSflow | SNVT_flow | Ext AF lw spd Extract air flow set point for the unit when running in low speed operation. | 0 | NV 215 | l/s
211 | 1107 | nvoEF_LSflow | SNVT_flow | Ext AF lw spd
212 | 1108 | nviSF_HSflow | SNVT_flow | Sup air flow high spd Supply air flow set point for the unit when running in high speed operation. | NV 209 | NV 217 | l/s
213 | 1109 | nvoSF_HSflow | SNVT_flow | Sup air flow high spd
214 | 1110 | nviEF_HSflow | SNVT_flow | Ext AF high spd Extract air flow set point for the unit when running in high speed operation. | NV 211 | NV 219 | l/s
215 | 1111 | nvoEF_HSflow | SNVT_flow | Ext AF high spd
216 | 1112 | nviSF_MaxflowBo | SNVT_flow | SA Max spd AF Boost Supply air flow max. limit for the unit when the low/high speed operation set point is altered by boosting function etc. | NV 213 | NV 89 | l/s
217 | 1113 | nvoSF_MaxflowBo | SNVT_flow | SA Max spd AF Boost
218 | 1114 | nviEF_MaxflowBo | SNVT_flow | EA Max spd AF Boost Extract air flow max. limit for the unit when the low/high speed operation set point is altered by boosting function etc. | NV 215 | NV 90 | l/s
219 | 1115 | nvoEF_MaxflowBo | SNVT_flow | EA Max spd AF Boost
220 | 1116 | nviSF_FlowZone | SNVT_lev_percent | SA AF reg zone Supply air flow regulation zone setting in % of the present air flow set point that the regulator is allowed to work within. | 1.00 | 10.00 | % | 7.50
221 | 1117 | nvoSF_FlowZone | SNVT_lev_percent | SA AF reg zone
222 | 1118 | nviEF_FlowZone | SNVT_lev_percent | EA AF reg zone Extract air flow regulation zone setting in % of the present air flow set point that the regulator is allowed to work within. | 1.00 | 10.00 | % | 7.50
223 | 1119 | nvoEF_FlowZone | SNVT_lev_percent | EA AF reg zone
224 | 1120 | nviSF_I-time | SNVT_time_sec | SA AF I-time Supply air flow regulator affection setting. | 1 | 1800 | s | 30
225 | 1121 | nvoSF_I-time | SNVT_time_sec | SA AF I-time
226 | 1122 | nviEF_I-time | SNVT_time_sec | EA AF I-time Extract air flow regulator affection setting. | 1 | 1800 | s | 30
227 | 1123 | nvoEF_I-time | SNVT_time_sec | EA AF I-time
Pressure regulation
228 | 1136 | nviSF_LSpressure | SNVT_press_p | SA Low spd pres Supply air duct pressure set point for the unit when running in low speed operation. | 0.0 | NV 233 | Pa
229 | 1137 | nvoSF_LSpressure | SNVT_press_p | SA Low spd pres
230 | 1138 | nviEF_LSpressure | SNVT_press_p | EA Low spd pres Extract air duct pressure set point for the unit when running in low speed operation. | 0.0 | NV 235 | Pa
231 | 1139 | nvoEF_LSpressure | SNVT_press_p | EA Low spd pres
232 | 1140 | nviSF_HSpressure | SNVT_press_p | SA High spd pres Supply air duct pressure for the unit when running in high speed operation. | NV 229 | NV 237 | Pa
233 | 1141 | nvoSF_HSpressure | SNVT_press_p | SA High spd pres
234 | 1142 | nviEF_HSpressure | SNVT_press_p | EA High spd pres Extract air duct pressure set point for the unit when running in high speed operation. | NV 231 | NV 239 | Pa
235 | 1143 | nvoEF_HSpressure | SNVT_press_p | EA High spd pres
236 | 1144 | nviSF_Maxpress | SNVT_press_p | SA Max spd pres Supply air duct pressure max. limit for the unit when the low/high speed operation set point is altered by boosting function etc. | NV 233 | 750.0 | Pa
237 | 1145 | nvoSF_Maxpress | SNVT_press_p | SA Max spd pres
238 | 1146 | nviEF_Maxpress | SNVT_press_p | EA Max spd pres Extract air duct pressure max. limit for the unit when the low/high speed operation set point is altered by boosting function etc. | NV 235 | 750.0 | Pa
239 | 1147 | nvoEF_Maxpress | SNVT_press_p | EA Max spd pres
240 | 1148 | nviSF_Maxspeed | SNVT_lev_percent | SA Max spd output sig Max. limit for the supply air fan speed when running in pressure regulation mode. | 0 | 100.00 | %
241 | 1149 | nvoSF_Maxspeed | SNVT_lev_percent | SA Max spd output sig
242 | 1150 | nviEF_Maxspeed | SNVT_lev_percent | EA Max spd output sig Max. limit for the extract air fan speed when running in pressure regulation mode. | 0 | 100.00 | %
243 | 1151 | nvoEF_Maxspeed | SNVT_lev_percent | EA Max spd output sig
244 | 1152 | nviSF_PressZone | SNVT_lev_percent | SA Pres reg zone Supply air pressure regulation zone setting in % of the present duct pressure set point that the regulator is allowed to work within. | 0 | 10.00 | % | 7.50
245 | 1153 | nvoSF_PressZone | SNVT_lev_percent | SA Pres reg zone
246 | 1154 | nviEF_PressZone | SNVT_lev_percent | EA Pres reg zone Extract air pressure regulation zone setting in % of the present duct pressure set point that the regulator is allowed to work within. | 0 | 10.00 | % | 7.50
247 | 1155 | nvoEF_PressZone | SNVT_lev_percent | EA Pres reg zone
248 | 1156 | nviSF_Press_I-t | SNVT_time_sec | SA Pres I-time Supply air pressure regulator affection setting. | 0 | 1800 | s | 30
249 | 1157 | nvoSF_Press_I-t | SNVT_time_sec | SA Pres I-time
250 | 1158 | nviEF_Press_I-t | SNVT_time_sec | EA Pres I-time Extract air pressure regulator affection setting. | 0 | 1800 | s | 30
251 | 1159 | nvoEF_Press_I-t | SNVT_time_sec | EA Pres I-time
Demand regulation
252 | 1172 | nviLS_demand | SNVT_lev_percent | Low spd dmnd Set point for the 0..10V input signal for the unit when running in low speed operation. | 0.00 | 100.00 | % | 50.00
253 | 1173 | nvoLS_demand | SNVT_lev_percent | Low spd dmnd
254 | 1174 | nviHS_demand | SNVT_lev_percent | High spd dmnd Set point for the 0..10V input signal for the unit when running in high speed operation. | 10.00 | 100.00 | % | 25.00
255 | 1175 | nvoHS_demand | SNVT_lev_percent | High spd dmnd
256 | 1176 | nviSF_Minflow | SNVT_flow | SA Min spd AF Supply air flow min. limit for the unit when the low/high speed operation set point is altered when running in fan regulation mode demand. | NV 87 | NV 261 | l/s
257 | 1177 | nvoSF_Minflow | SNVT_flow | SA Min spd AF
258 | 1178 | nviEF_Minflow | SNVT_flow | EA Min spd AF Extract air flow min. limit for the unit when the low/high speed operation set point is altered when running in fan regulation mode demand. | NV 88 | NV 263 | l/s
259 | 1179 | nvoEF_Minflow | SNVT_flow | EA Min spd AF
260 | 1180 | nviSF_MaxflowDe | SNVT_flow | SA Max spd AF demand Supply air flow max limit for the unit when the low/high speed operation set point is altered when running in fan regulation mode demand. | NV 257 | NV 89 | l/s
261 | 1181 | nvoSF_MaxflowDe | SNVT_flow | SA Max spd AF demand
262 | 1182 | nviEF_MaxflowDe | SNVT_flow | EA Max spd AF demand Extract air flow max. limit for the unit when the low/high speed operation set point is altered when running in fan regulation mode demand. | NV 259 | NV 90 | l/s
263 | 1183 | nvoEF_MaxflowDe | SNVT_flow | EA Max spd AF demand
264 | 1184 | nviDemand_P-b | SNVT_lev_percent | Dmnd P-band Supply air demand regulator P-band setting. | 1.00 | 100.00 | % | 40.00
265 | 1185 | nvoDemand_P-b | SNVT_lev_percent | Dmnd P-band
266 | 1186 | nviDemand_I-t | SNVT_time_sec | Dmnd I-time Supply air demand regulator affection setting. | 1 | 1800 | s | 1200
267 | 1187 | nvoDemand_I-t | SNVT_time_sec | Dmnd I-time
Slave controlled regulation
268 | 1198 | nviSlaveOffFact | SNVT_lev_percent | Slave offset factor | 50.00 | 200.00 | % | 0.00
269 | 1199 | nvoSlaveOffFact | SNVT_lev_percent | Slave offset factor
Fans OA temp compensation
270 | 1204 | nviOutCmpTempFu | SNVT_count | Outd Temp Cmp func 0=Inactive, 1=Active at low speed, 2=Active at high speed, 3=Active at low and high speed. | 0 | 3 |  | 0
271 | 1205 | nvoOutCmpTempFu | SNVT_count | Outd Temp Cmp func
272 | 1206 | nviOutCmpTempX1 | SNVT_temp_p | Outd Temp Cmp X1 | -50.00 | NV 275 | °C | -20.00
273 | 1207 | nvoOutCmpTempX1 | SNVT_temp_p | Outd Temp Cmp X1
274 | 1208 | nviOutCmpTempX2 | SNVT_temp_p | Outd Temp Cmp X2 | NV 273 | NV 277 | °C | -10.00
275 | 1209 | nvoOutCmpTempX2 | SNVT_temp_p | Outd Temp Cmp X2
276 | 1210 | nviOutCmpTempX3 | SNVT_temp_p | Outd Temp Cmp X3 | NV 275 | NV 279 | °C | 10.00
277 | 1211 | nvoOutCmpTempX3 | SNVT_temp_p | Outd Temp Cmp X3
278 | 1212 | nviOutCmpTempX4 | SNVT_temp_p | Outd Temp Cmp X4 | NV 277 | 50.00 | °C | 20.00
279 | 1213 | nvoOutCmpTempX4 | SNVT_temp_p | Outd Temp Cmp X4
280 | 1214 | nviOutCmpFlwY1SA | SNVT_flow | Outd Temp Cmp Y1 SA Flow | NV 87 | NV 89 | l/s
281 | 1215 | nvoOutCmpFlwY1SA | SNVT_flow | Outd Temp Cmp Y1 SA Flow
282 | 1216 | nviOutCmpFlwY2SA | SNVT_flow | Outd Temp Cmp Y2 SA Flow | NV 87 | NV 89 | l/s
283 | 1217 | nvoOutCmpFlwY2SA | SNVT_flow | Outd Temp Cmp Y2 SA Flow
284 | 1218 | nviOutCmpFlwY3SA | SNVT_flow | Outd Temp Cmp Y3 SA Flow | NV 87 | NV 89 | l/s
285 | 1219 | nvoOutCmpFlwY3SA | SNVT_flow | Outd Temp Cmp Y3 SA Flow
286 | 1220 | nviOutCmpFlwY4SA | SNVT_flow | Outd Temp Cmp Y4 SA Flow | NV 87 | NV 89 | l/s
287 | 1221 | nvoOutCmpFlwY4SA | SNVT_flow | Outd Temp Cmp Y4 SA Flow
288 | 1222 | nviOutCmpFlwY1EA | SNVT_flow | Outd Temp Cmp Y1 EA Flow | NV 88 | NV 90 | l/s
289 | 1223 | nvoOutCmpFlwY1EA | SNVT_flow | Outd Temp Cmp Y1 EA Flow
290 | 1224 | nviOutCmpFlwY2EA | SNVT_flow | Outd Temp Cmp Y2 EA Flow | NV 88 | NV 90 | l/s
291 | 1225 | nvoOutCmpFlwY2EA | SNVT_flow | Outd Temp Cmp Y2 EA Flow
292 | 1226 | nviOutCmpFlwY3EA | SNVT_flow | Outd Temp Cmp Y3 EA Flow | NV 88 | NV 90 | l/s
293 | 1227 | nvoOutCmpFlwY3EA | SNVT_flow | Outd Temp Cmp Y3 EA Flow
294 | 1228 | nviOutCmpFlwY4EA | SNVT_flow | Outd Temp Cmp Y4 EA Flow | NV 88 | NV 90 | l/s
295 | 1229 | nvoOutCmpFlwY4EA | SNVT_flow | Outd Temp Cmp Y4 EA Flow
296 | 1230 | nviOutCmpPrsY1SA | SNVT_press_p | Outd Temp Cmp Y1 SA Press | 20.0 | 750.0 | Pa | 100.0
297 | 1231 | nvoOutCmpPrsY1SA | SNVT_press_p | Outd Temp Cmp Y1 SA Press
298 | 1232 | nviOutCmpPrsY2SA | SNVT_press_p | Outd Temp Cmp Y2 SA Press | 20.0 | 750.0 | Pa | 100.0
299 | 1233 | nvoOutCmpPrsY2SA | SNVT_press_p | Outd Temp Cmp Y2 SA Press
300 | 1234 | nviOutCmpPrsY3SA | SNVT_press_p | Outd Temp Cmp Y3 SA Press | 20.0 | 750.0 | Pa | 100.0
301 | 1235 | nvoOutCmpPrsY3SA | SNVT_press_p | Outd Temp Cmp Y3 SA Press
302 | 1236 | nviOutCmpPrsY4SA | SNVT_press_p | Outd Temp Cmp Y4 SA Press | 20.0 | 750.0 | Pa | 100.0
303 | 1237 | nvoOutCmpPrsY4SA | SNVT_press_p | Outd Temp Cmp Y4 SA Press
304 | 1238 | nviOutCmpPrsY1EA | SNVT_press_p | Outd Temp Cmp Y1 EA Press | 20.0 | 750.0 | Pa | 100.0
305 | 1239 | nvoOutCmpPrsY1EA | SNVT_press_p | Outd Temp Cmp Y1 EA Press
306 | 1240 | nviOutCmpPrsY2EA | SNVT_press_p | Outd Temp Cmp Y2 EA Press | 20.0 | 750.0 | Pa | 100.0
307 | 1241 | nvoOutCmpPrsY2EA | SNVT_press_p | Outd Temp Cmp Y2 EA Press
308 | 1242 | nviOutCmpPrsY3EA | SNVT_press_p | Outd Temp Cmp Y3 EA Press | 20.0 | 750.0 | Pa | 100.0
309 | 1243 | nvoOutCmpPrsY3EA | SNVT_press_p | Outd Temp Cmp Y3 EA Press
310 | 1244 | nviOutCmpPrsY4EA | SNVT_press_p | Outd Temp Cmp Y4 EA Press | 20.0 | 750.0 | Pa | 100.0
311 | 1245 | nvoOutCmpPrsY4EA | SNVT_press_p | Outd Temp Cmp Y4 EA Press
Fans down regulation
312 | 1254 | nviDownRegFunc | SNVT_count | Fans down reg func 0=Inactive, 1=SA, 2=SA and EA | 0 | 2 |  | 1
313 | 1255 | nvoDownRegFunc | SNVT_count | Fans down reg func
314 | 1256 | nviDownReg_NZ | SNVT_temp_p | Fans down reg ntrl zone | 0.00 | 10.00 | K | 0.00
315 | 1257 | nvoDownReg_NZ | SNVT_temp_p | Fans down reg ntrl zone
316 | 1258 | nviDownReg_P-b | SNVT_temp_p | Fans down reg P-band | 1.00 | 10.00 | K | 5.00
317 | 1259 | nvoDownReg_P-b | SNVT_temp_p | Fans down reg P-band
318 | 1260 | nviDownReg_I-t | SNVT_time_sec | Fans down reg I-time | 1 | 1800 | s | 30
319 | 1261 | nvoDownReg_I-t | SNVT_time_sec | Fans down reg I-time
AHU Temperature regulation
320 | 1328 | nviTempregmode | SNVT_count | Temp reg mode 1=ERS-1, 2=ERS-2, 3=SA, 4=EA, 5=ORS, 6=ORE | 1 | 6 |  | 3
321 | 1329 | nvoTempregmode | SNVT_count | Temp reg mode
ERS-1 reg.
322 | 1332 | nviERS1step | SNVT_count | ERS 1 Step Curve setting according to the diagram for ERS 1. | 1 | 4 |  | 2
323 | 1333 | nvoERS1step | SNVT_count | ERS 1 Step
324 | 1334 | nviERS1diff | SNVT_temp_p | SA temp diff set ERS 1 Supply air temp difference setting according to the diagram for ERS 1. | 1.00 | 7.00 | K | 2.00
325 | 1335 | nvoERS1diff | SNVT_temp_p | SA temp diff set ERS 1
326 | 1336 | nviERS1brkpnt | SNVT_temp_p | ERS 1 Brkpnt Breakpoint temp setting according to the diagram for ERS 1. | 12.00 | 26.00 | °C | 22.00
327 | 1337 | nvoERS1brkpnt | SNVT_temp_p | ERS 1 Brkpnt
ERS-2 reg.
328 | 1342 | nviERS2_X1 | SNVT_temp_p | ERS 2 Brkpnt_X1 Breakpoint X1 setting according to the diagram for ERS 2. | 10.00 | NV 331 | °C | 15.00
329 | 1343 | nvoERS2_X1 | SNVT_temp_p | ERS 2 Brkpnt_X1
330 | 1344 | nviERS2_X2 | SNVT_temp_p | ERS 2 Brkpnt_X2 Breakpoint X2 setting according to the diagram for ERS 2. | NV 329 | NV 333 | °C | 20.00
331 | 1345 | nvoERS2_X2 | SNVT_temp_p | ERS 2 Brkpnt_X2
332 | 1346 | nviERS2_X3 | SNVT_temp_p | ERS 2 Brkpnt_X3 Breakpoint X3 setting according to the diagram for ERS 2. | NV 331 | NV 335 | °C | 22.00
333 | 1347 | nvoERS2_X3 | SNVT_temp_p | ERS 2 Brkpnt_X3
334 | 1348 | nviERS2_X4 | SNVT_temp_p | ERS 2 Brkpnt_X4 Breakpoint X4 setting according to the diagram for ERS 2. | NV 333 | 40.00 | °C | 24.00
335 | 1349 | nvoERS2_X4 | SNVT_temp_p | ERS 2 Brkpnt_X4
336 | 1350 | nviERS2_Y1 | SNVT_temp_p | ERS 2 Brkpnt_Y1 Breakpoint Y1 setting according to the diagram for ERS 2. | 10.00 | 40.00 | °C | 20.00
337 | 1351 | nvoERS2_Y1 | SNVT_temp_p | ERS 2 Brkpnt_Y1
338 | 1352 | nviERS2_Y2 | SNVT_temp_p | ERS 2 Brkpnt_Y2 Breakpoint Y2 setting according to the diagram for ERS 2. | 10.00 | 40.00 | °C | 18.00
339 | 1353 | nvoERS2_Y2 | SNVT_temp_p | ERS 2 Brkpnt_Y2
340 | 1354 | nviERS2_Y3 | SNVT_temp_p | ERS 2 Brkpnt_Y3 Breakpoint Y3 setting according to the diagram for ERS 2. | 10.00 | 40.00 | °C | 14.00
341 | 1355 | nvoERS2_Y3 | SNVT_temp_p | ERS 2 Brkpnt_Y3
342 | 1356 | nviERS2_Y4 | SNVT_temp_p | ERS 2 Brkpnt_Y4 Breakpoint Y4 setting according to the diagram for ERS 2. | 10.00 | 40.00 | °C | 12.00
343 | 1357 | nvoERS2_Y4 | SNVT_temp_p | ERS 2 Brkpnt_Y4
SA Reg.
344 | 2 | nviSetpoint | SNVT_temp_p | Temp stpnt Input (absolute) Supply air temperature setting, for supply air temp regulation mode. | 10.00 | 40.00 | °C | 21.00
345 | 1363 | nvoSetpoint | SNVT_temp_p | Temp stpnt (absolute)
EA Reg.
346 | 1368 | nviEAtempset | SNVT_temp_p | EA Temp Extract air/room temperature setting, for Extract air/room temp regulation mode. | 10.00 | 40.00 | °C | 21.00
347 | 1369 | nvoEAtempset | SNVT_temp_p | EA Temp
348 | 1370 | nviMinSAtemp | SNVT_temp_p | SA Min temp Supply air min. set point during EA/room regulation mode. | 8.00 | 20.00 | °C | 16.00
349 | 1371 | nvoMinSAtemp | SNVT_temp_p | SA Min temp
350 | 1372 | nviMaxSAtemp | SNVT_temp_p | SA Max temp Supply air max. set point during EA/room regulation mode. | 16.00 | 50.00 | °C | 28.00
351 | 1373 | nvoMaxSAtemp | SNVT_temp_p | SA Max temp
352 | 1374 | nviEA_Reg_P-b | SNVT_temp_p | EA reg P-band | 1.00 | 10.00 | K | 5.00
353 | 1375 | nvoEA_Reg_P-b | SNVT_temp_p | EA reg P-band
354 | 1376 | nviEA_Reg_I-t | SNVT_time_sec | EA reg I-time | 1 | 1800 | s | 30
355 | 1377 | nvoEA_Reg_I-t | SNVT_time_sec | EA reg I-time
ORS Reg.
356 | 1382 | nviORS_X1 | SNVT_temp_p | ORS Brkpnt_X1 Breakpoint X1 setting according to the diagram for ORS. | -5.00 | NV 359 | °C | -20.00
357 | 1383 | nvoORS_X1 | SNVT_temp_p | ORS Brkpnt_X1
358 | 1384 | nviORS_X2 | SNVT_temp_p | ORS Brkpnt_X2 Breakpoint X2 setting according to the diagram for ORS. | NV 357 | NV 361 | °C | -10.00
359 | 1385 | nvoORS_X2 | SNVT_temp_p | ORS Brkpnt_X2
360 | 1386 | nviORS_X3 | SNVT_temp_p | ORS Brkpnt_X3 Breakpoint X3 setting according to the diagram for ORS. | NV 359 | NV 363 | °C | 10.00
361 | 1387 | nvoORS_X3 | SNVT_temp_p | ORS Brkpnt_X3
362 | 1388 | nviORS_X4 | SNVT_temp_p | ORS Brkpnt_X4 Breakpoint X4 setting according to the diagram for ORS. | NV 361 | 50.00 | °C | 20.00
363 | 1389 | nvoORS_X4 | SNVT_temp_p | ORS Brkpnt_X4
364 | 1390 | nviORS_Y1 | SNVT_temp_p | ORS Brkpnt_Y1 Breakpoint Y1 setting according to the diagram for ORS. | 10.00 | 40.00 | °C | 21.50
365 | 1391 | nvoORS_Y1 | SNVT_temp_p | ORS Brkpnt_Y1
366 | 1392 | nviORS_Y2 | SNVT_temp_p | ORS Brkpnt_Y2 Breakpoint Y2 setting according to the diagram for ORS. | 10.00 | 40.00 | °C | 21.50
367 | 1393 | nvoORS_Y2 | SNVT_temp_p | ORS Brkpnt_Y2
368 | 1394 | nviORS_Y3 | SNVT_temp_p | ORS Brkpnt_Y3 Breakpoint Y3 setting according to the diagram for ORS. | 10.00 | 40.00 | °C | 21.50
369 | 1395 | nvoORS_Y3 | SNVT_temp_p | ORS Brkpnt_Y3
370 | 1396 | nviORS_Y4 | SNVT_temp_p | ORS Brkpnt_Y4 Breakpoint Y4 setting according to the diagram for ORS. | 10.00 | 40.00 | °C | 21.50
371 | 1397 | nvoORS_Y4 | SNVT_temp_p | ORS Brkpnt_Y4
ORE Reg.
372 | 1402 | nviORE_X1 | SNVT_temp_p | ORE Brkpnt_X1 Breakpoint X1 setting according to the diagram for ORE. | -5.00 | NV 375 | °C | -20.00
373 | 1403 | nvoORE_X1 | SNVT_temp_p | ORE Brkpnt_X1
374 | 1404 | nviORE_X2 | SNVT_temp_p | ORE Brkpnt_X2 Breakpoint X2 setting according to the diagram for ORE. | NV 373 | NV 377 | °C | -10.00
375 | 1405 | nvoORE_X2 | SNVT_temp_p | ORE Brkpnt_X2
376 | 1406 | nviORE_X3 | SNVT_temp_p | ORE Brkpnt_X3 Breakpoint X3 setting according to the diagram for ORE. | NV 375 | NV 379 | °C | 10.00
377 | 1407 | nvoORE_X3 | SNVT_temp_p | ORE Brkpnt_X3
378 | 1408 | nviORE_X4 | SNVT_temp_p | ORE Brkpnt_X4 Breakpoint X4 setting according to the diagram for ORE. | NV 377 | 50.00 | °C | 20.00
379 | 1409 | nvoORE_X4 | SNVT_temp_p | ORE Brkpnt_X4
380 | 1410 | nviORE_Y1 | SNVT_temp_p | ORE Brkpnt_X4 Breakpoint Y1 setting according to the diagram for ORE. | 10.00 | 40.00 | °C | 21.50
381 | 1411 | nvoORE_Y1 | SNVT_temp_p | ORE Brkpnt_Y1
382 | 1412 | nviORE_Y2 | SNVT_temp_p | ORE Brkpnt_Y2 Breakpoint Y2 setting according to the diagram for ORE. | 10.00 | 40.00 | °C | 21.50
383 | 1413 | nvoORE_Y2 | SNVT_temp_p | ORE Brkpnt_Y2
384 | 1414 | nviORE_Y3 | SNVT_temp_p | ORE Brkpnt_Y3 Breakpoint Y3 setting according to the diagram for ORE. | 10.00 | 40.00 | °C | 21.50
385 | 1415 | nvoORE_Y3 | SNVT_temp_p | ORE Brkpnt_Y3
386 | 1416 | nviORE_Y4 | SNVT_temp_p | ORE Brkpnt_Y4 Breakpoint Y4 setting according to the diagram for ORE. | 10.00 | 40.00 | °C | 21.50
387 | 1417 | nvoORE_Y4 | SNVT_temp_p | ORE Brkpnt_Y4
AHU external sensors
388 | 1430 | nviRoomTempExtFu | SNVT_count | EA/Room temp ext func 0=Average, 1=Min, 2=Max | 0 | 2 |  | 0
389 | 1431 | nvoRoomTempExtFu | SNVT_count | EA/Room temp ext func
390 | 1432 | nviRoomTempBMSFu | SNVT_count | EA/Room temp from BMS func | 0 | 1 |  | 0
391 | 1433 | nvoRoomTempBMSFu | SNVT_count | EA/Room temp from BMS func
392 | 1434 | nviRoomTempBMS | SNVT_temp_p | EA/Room temp from BMS | -55.00 | 125.00 | °C | 0.00
393 | 1435 | nvoRoomTempBMS | SNVT_temp_p | EA/Room temp from BMS
394 | 1436 | nviRoomTempBMSAl | SNVT_time_min | EA/Room temp from BMS alarm | 0 | 9999 | min | 5
395 | 1437 | nvoRoomTempBMSAl | SNVT_time_min | EA/Room temp from BMS alarm
396 | 1450 | nviOutdTempExtFu | SNVT_count | Outdoor temp ext func 0=Average, 1=Min, 2=Max | 0 | 2 |  | 0
397 | 1451 | nvoOutdTempExtFu | SNVT_count | Outdoor temp ext func
398 | 1452 | nviOutdTempBMSFu | SNVT_count | Outdoor temp from BMS func | 0 | 1 |  | 0
399 | 1453 | nvoOutdTempBMSFu | SNVT_count | Outdoor temp from BMS func
400 | 1454 | nviOutdTempBMS | SNVT_temp_p | Outdoor temp from BMS | -55.00 | 125.00 | °C | 0.00
401 | 1455 | nvoOutdTempBMS | SNVT_temp_p | Outdoor temp from BMS
402 | 1456 | nviOutdTempBMSAl | SNVT_time_min | Outdoor temp from BMS alarm | 0 | 9999 | min | 5
403 | 1457 | nvoOutdTempBMSAl | SNVT_time_min | Outdoor temp from BMS alarm
AHU Heat exchange
404 | 1462 | nviRHX_defr_func | SNVT_switch | Defrost Heat X Act Setting for activating the defrost function for the rotary heat exchanger. | 0 | 1 |  | 0
405 | 1463 | nvoRHX_defr_func | SNVT_switch | Defrost Heat X
406 | 1464 | nviRHX_defr_cal | SNVT_switch | Defrost Heat X Cal | 0 | 1 |  | 0
407 | 1465 | nvoRHX_defr_cal | SNVT_switch | Defrost Heat X Cal
408 | 1466 | nviRHX_defr_sta | SNVT_press_p | Defrost Heat X start | 30.0 | 100.0 | Pa | 50.0
409 | 1467 | nvoRHX_defr_sta | SNVT_press_p | Defrost Heat X start
410 | 1472 | nviRHX_COC_func | SNVT_switch | Carry over cont Heat X Act Setting for activating the carry over control function for the rotary heat exchanger. | 0 | 1 |  | 0
411 | 1473 | nvoRHX_COC_func | SNVT_switch | Carry over cont Heat X
412 | 1478 | nviRHX_MinEAtmpF | SNVT_switch | Min EA temp Heat X Act | 0 | 1 |  | 0
413 | 1479 | nvoRHX_MinEAtmpF | SNVT_switch | Min EA temp Heat X
414 | 1480 | nviRHX_MinEAtmpS | SNVT_temp_p | Min EA temp Heat X stpnt | -40.00 | 20.00 | °C | 5.00
415 | 1481 | nvoRHX_MinEAtmpS | SNVT_temp_p | Min EA temp Heat X stpnt
416 | 1482 | nviRHX_MinEAtmpP | SNVT_temp_p | Min EA temp Heat X P-band | 1.00 | 40.00 | K | 8.00
417 | 1483 | nvoRHX_MinEAtmpP | SNVT_temp_p | Min EA temp Heat X P-band
418 | 1484 | nviRHX_MinEAtmpI | SNVT_time_sec | Min EA temp Heat X I-time | 0 | 30000 | s | 30
419 | 1485 | nvoRHX_MinEAtmpI | SNVT_time_sec | Min EA temp Heat X I-time
420 | 1524 | nviPCHX_defr_lim | SNVT_temp_p | P/C.HX.defrost limit PHX is default 3°C, CHX is default 5°C. | -10.00 | 5.00 | °C
421 | 1525 | nvoPCHX_defr_lim | SNVT_temp_p | P/C.HX.defrost limit
422 | 1526 | nviPCHX_defr_P-b | SNVT_temp_p | P/C.HX.defrost P-band | 1.00 | 40.00 | K | 20.00
423 | 1527 | nvoPCHX_defr_P-b | SNVT_temp_p | P/C.HX.defrost P-band
424 | 1528 | nviPCHX_defr_I-t | SNVT_time_sec | P/C.HX.defrost I-time | 1 | 600 | s | 60
425 | 1529 | nvoPCHX_defr_I-t | SNVT_time_sec | P/C.HX.defrost I-time
426 | 1538 | nviHX_tmp_reg_Pb | SNVT_temp_p | P/C.HX.defrost P-band | 1.00 | 10.00 | K | 6.00
427 | 1539 | nvoHX_tmp_reg_Pb | SNVT_temp_p | P/C.HX.defrost P-band
428 | 1540 | nviHX_tmp_reg_It | SNVT_time_sec | P/C.HX.defrost I-time | 1 | 1800 | s | 50
429 | 1541 | nvoHX_tmp_reg_It | SNVT_time_sec | P/C.HX.defrost I-time
AHU Heat/Cool
430 | 1550 | nviReHeat_P-band | SNVT_temp_p | ReHeat P-band | 1.00 | 10.00 | K | 8.00
431 | 1551 | nvoReHeat_P-band | SNVT_temp_p | ReHeat P-band
432 | 1552 | nviReHeat_I-time | SNVT_time_sec | ReHeat I-time | 1 | 1800 | s | 70
433 | 1553 | nvoReHeat_I-time | SNVT_time_sec | ReHeat I-time
434 | 1572 | nviEXreg_func | SNVT_count | Extra reg seq func 0=Inactive, 1=Heat, 2=Cool, 3=Heat and Cool. | 0 | 3 |  | 0
435 | 1573 | nvoEXreg_func | SNVT_count | Extra reg seq func
436 | 1574 | nviEXreg_OP_func | SNVT_count | Extra reg seq output func 0=0-10V, 1=10-0V | 0 | 1 |  | 0
437 | 1575 | nvoEXreg_OP_func | SNVT_count | Extra reg seq output func
438 | 1576 | nviEXreg_H_MaxOP | SNVT_lev_percent | Extra reg seq heat max output Maximum output signal setting for the extra regulation sequence. | 0.00 | 100.00 | % | 100.00
439 | 1577 | nvoEXreg_H_MaxOP | SNVT_lev_percent | Extra reg seq heat max output
440 | 1578 | nviEXreg_C_MaxOP | SNVT_lev_percent | Extra reg seq cool max output Maximum output signal setting for the extra regulation sequence. | 0.00 | 100.00 | % | 100.00
441 | 1579 | nvoEXreg_C_MaxOP | SNVT_lev_percent | Extra reg seq cool max output
442 | 1580 | nviEXreg_H_P-b | SNVT_temp_p | Extra reg seq heat P-band | 1.00 | 10.00 | K | 8
443 | 1581 | nvoEXreg_H_P-b | SNVT_temp_p | Extra reg seq heat P-band
444 | 1582 | nviEXreg_H_I-t | SNVT_time_sec | Extra reg seq heat I-time | 1 | 1800 | s | 70
445 | 1583 | nvoEXreg_H_I-t | SNVT_time_sec | Extra reg seq heat I-time
446 | 1584 | nviEXreg_C_P-b | SNVT_temp_p | Extra reg seq cool P-band | 1.00 | 10.00 | K | 6
447 | 1585 | nvoEXreg_C_P-b | SNVT_temp_p | Extra reg seq cool P-band
448 | 1586 | nviEXreg_C_I-t | SNVT_time_sec | Extra reg seq cool I-time | 1 | 1800 | s | 60
449 | 1587 | nvoEXreg_C_I-t | SNVT_time_sec | Extra reg seq cool I-time
450 | 1600 | nviEXreg_Pro_Fu | SNVT_switch | Extra reg temp protection func | 0 | 1 |  | 0 | 1.10
451 | 1601 | nvoEXreg_Pro_Fu | SNVT_switch | Extra reg temp protection func
452 | 1602 | nviEXreg_Pro_Tmp | SNVT_temp_p | Extra reg temp protection temp | -50.00 | 100.00 | °C | 0.00 | 1.10
453 | 1603 | nvoEXreg_Pro_Tmp | SNVT_temp_p | Extra reg temp protection temp
454 | 1604 | nviEXreg_Pro_Al | SNVT_time_min | Extra reg temp protection alarm | 0 | 9999 | min | 5 | 1.10
455 | 1605 | nvoEXreg_Pro_Al | SNVT_time_min | Extra reg temp protection alarm
456 | 1620 | nviCool_reg_func | SNVT_count | Cool on/off regulation func 0=Inactive, 1=1 step, 2=2 steps, 3=3 steps. | 0 | 3 |  | 0
457 | 1621 | nvoCool_reg_func | SNVT_count | Cool on/off regulation func
458 | 1622 | nviCool_SA_NZ | SNVT_temp_p | Cool SA neutral zone | 0.50 | 10.00 | K | 2.00
459 | 1623 | nvoCool_SA_NZ | SNVT_temp_p | Cool SA neutral zone
460 | 1624 | nviCool_EA_NZ | SNVT_temp_p | Cool EA neutral zone | 0.50 | 10.00 | K | 2.00
461 | 1625 | nvoCool_EA_NZ | SNVT_temp_p | Cool EA neutral zone
462 | 1626 | nviCoolLimit1 | SNVT_temp_p | Cool Outd temp limit 1 | 0.00 | 30.00 | °C | 15.00
463 | 1627 | nvoCoolLimit1 | SNVT_temp_p | Cool Outd temp limit 1
464 | 1628 | nviCoolLimit2 | SNVT_temp_p | Cool Outd temp limit 2 | 0.00 | 30.00 | °C | 18.00
465 | 1629 | nvoCoolLimit2 | SNVT_temp_p | Cool Outd temp limit 2
466 | 1630 | nviCoolLimit3 | SNVT_temp_p | Cool Outd temp limit 3 | 0.00 | 30.00 | °C | 20.00
467 | 1631 | nvoCoolLimit3 | SNVT_temp_p | Cool Outd temp limit 3
468 | 1632 | nviSFcoolMinflow | SNVT_flow | SA Cool min air flow | 0 | NV 89 | l/s
469 | 1633 | nvoSFcoolMinflow | SNVT_flow | SA Cool min air flow
470 | 1634 | nviEFcoolMinflow | SNVT_flow | EA Cool min air flow | 0 | NV 90 | l/s
471 | 1635 | nvoEFcoolMinflow | SNVT_flow | EA Cool min air flow
472 | 1636 | nviCool_restart | SNVT_time_min | Cool restart time Setting of cool restart time between start-start. | 0 | 15 | min | 5
473 | 1637 | nvoCool_restart | SNVT_time_min | Cool restart time
474 | 1638 | nviCoolstep_time | SNVT_time_min | Cool step time Setting of on/off cooling and COOL DX time delay between steps. | 0 | 10 | min | 5
475 | 1639 | nvoCoolstep_time | SNVT_time_min | Cool step time
476 | 1640 | nviCoolStillTime | SNVT_time_min | Cool stand still time Setting of on/off cooling and COOL DX time delay before stop-start | 0 | 20 | min | 5
477 | 1641 | nvoCoolStillTime | SNVT_time_min | Cool stand still time
478 | 1642 | nviCool_P-band | SNVT_temp_p | Cool P-band | 1.00 | 10.00 | K | 6
479 | 1643 | nvoCool_P-band | SNVT_temp_p | Cool P-band
480 | 1644 | nviCool_I-time | SNVT_time_sec | Cool I-time | 1 | 1800 | s | 60
481 | 1645 | nvoCool_I-time | SNVT_time_sec | Cool I-time
Summer night cool/Intermittent night heat /Morning boost
482 | 1666 | nviNC_func | SNVT_switch | Smr Nght Cool Act | 0 | 1 |  | 0
483 | 1667 | nvoNC_func | SNVT_switch | Smr Nght Cool
484 | 1668 | nviNC_start_h | SNVT_time_hour | Smr nght cool strt hour | 0 | 23 | h | 23
485 | 1669 | nvoNC_start_h | SNVT_time_hour | Smr nght cool strt hour
486 | 1670 | nviNC_start_m | SNVT_time_min | Smr nght cool strt min | 0 | 59 | min | 0
487 | 1671 | nvoNC_start_m | SNVT_time_min | Smr nght cool strt min
488 | 1672 | nviNC_stop_h | SNVT_time_hour | Smr nght cool stop hour | 0 | 23 | h | 23
489 | 1673 | nvoNC_stop_h | SNVT_time_hour | Smr nght cool stop hour
490 | 1674 | nviNC_stop_m | SNVT_time_min | Smr nght cool stop min | 0 | 59 | min | 0
491 | 1675 | nvoNC_stop_m | SNVT_time_min | Smr nght cool stop min
492 | 1676 | nviNC_OUTlimit | SNVT_temp_p | Smr nght cl outd temp lmt | -5.00 | 15.00 | °C | 10.00
493 | 1677 | nvoNC_OUTlimit | SNVT_temp_p | Smr nght cl outd temp lmt
494 | 1678 | nviNC_starttemp | SNVT_temp_p | Smr Nght cl room strt temp | 17.00 | 27.00 | °C | 22.00
495 | 1679 | nvoNC_starttemp | SNVT_temp_p | Smr Nght cl room strt temp
496 | 1680 | nviNC_stoptemp | SNVT_temp_p | Smr Nght cl room stop temp | 12.00 | 22.00 | °C | 16.00
497 | 1681 | nvoNC_stoptemp | SNVT_temp_p | Smr Nght cl room stop temp
498 | 1682 | nviNC_SAtempset | SNVT_temp_p | Smr nght cl SA temp | 0.00 | 20.00 | °C | 10.00
499 | 1683 | nvoNC_SAtempset | SNVT_temp_p | Smr nght cl SA temp
500 | 1690 | nviNH_func | SNVT_switch | Intrmt Nght Heat Act | 0 | 1 |  | 0
501 | 1691 | nvoNH_func | SNVT_switch | Intrmt Nght Heat
502 | 1692 | nviNH_SAflowset | SNVT_flow | Int Nght ht SA airflow | NV 87 | NV 89 | l/s
503 | 1693 | nvoNH_SAflowset | SNVT_flow | Int Nght ht SA airflow
504 | 1694 | nviNH_SApress | SNVT_press_p | Int.Night heat SA press set | 20 | 750 | Pa | 100
505 | 1695 | nvoNH_SApress | SNVT_press_p | Int.Night heat SA press set
506 | 1696 | nviNH_starttemp | SNVT_temp_p | Int Nght ht room strt temp | 5.00 | NV 509 | °C | 16.00
507 | 1697 | nvoNH_starttemp | SNVT_temp_p | Int Nght ht room strt temp
508 | 1698 | nviNH_stoptemp | SNVT_temp_p | Int Nght ht room stop temp | NV 507 | 25.00 | °C | 18.00
509 | 1699 | nvoNH_stoptemp | SNVT_temp_p | Int Nght ht room stop temp
510 | 1700 | nviNH_SAtempset | SNVT_temp_p | Int Nght ht SA temp | 5.00 | 50.00 | °C | 28.00
511 | 1701 | nvoNH_SAtempset | SNVT_temp_p | Int Nght ht SA temp
512 | 1708 | nviMB_func | SNVT_switch | Mrn bst Act | 0 | 1 |  | 0
513 | 1709 | nvoMB_func | SNVT_switch | Mrn bst
514 | 1710 | nviMornboost_h | SNVT_time_hour | Mrn bst hour | 0 | 23 | h | 0
515 | 1711 | nvoMornboost_h | SNVT_time_hour | Mrn bst hour
516 | 1712 | nviMornboost_m | SNVT_time_min | Mrn bst min | 0 | 59 | min | 0
517 | 1713 | nvoMornboost_m | SNVT_time_min | Mrn bst min
518 | 1714 | nviMB_SAflowset | SNVT_flow | Mrn bst SA airflow | NV 87 | NV 89 | l/s
519 | 1715 | nvoMB_SAflowset | SNVT_flow | Mrn bst SA airflow
520 | 1716 | nviMB_SApress | SNVT_press_p | Mrn bst SA press set | 20 | 750 | Pa | 100
521 | 1717 | nvoMB_SApress | SNVT_press_p | Mrn bst SA press set
Cooling boost/heating boost
522 | 1724 | nviC_boostMode | SNVT_count | Cooling bst reg mode 0=Inactive, 1=Comfort, 2=Economy, 3=Sequence, 4=Comfort and Economy, 5=Economy and Sequence | 0 | 5 |  | 0
523 | 1725 | nvoC_boostMode | SNVT_count | Cooling bst reg mode
524 | 1726 | nviC_boostStart | SNVT_temp_p | Cooling bst com start limit | 2.00 | 10.00 | K | 3.00
525 | 1727 | nvoC_boostStart | SNVT_temp_p | Cooling bst com start limit
526 | 1728 | nviC_boostSpeed | SNVT_lev_percent | Cooling bst com reg speed | 1 | 25 | %/s | 4
527 | 1729 | nvoC_boostSpeed | SNVT_lev_percent | Cooling bst com reg speed
528 | 1730 | nviC_boostP-band | SNVT_temp_p | Cooling bst P-band | 1 | 10.00 | K
529 | 1731 | nvoC_boostP-band | SNVT_temp_p | Cooling bst P-band
530 | 1732 | nviC_boostI-time | SNVT_time_sec | Cooling bst I-time | 1 | 1800 | s
531 | 1733 | nvoC_boostI-time | SNVT_time_sec | Cooling bst I-time
532 | 1738 | nviH_boostmode | SNVT_count | Heating bst reg mode | 0 | 1 |  | 0
533 | 1739 | nvoH_boostmode | SNVT_count | Heating bst reg mode
534 | 1740 | nviH_boostStart | SNVT_temp_p | Heating bst com start limit | 2.00 | 10.00 | K | 3.00
535 | 1741 | nvoH_boostStart | SNVT_temp_p | Heating bst com start limit
536 | 1742 | nviH_boostSpeed | SNVT_lev_percent | Heating bst com reg speed | 1 | 25 | %/s | 4
537 | 1743 | nvoH_boostSpeed | SNVT_lev_percent | Heating bst com reg speed
Xzone function
538 | 1748 | nviXZ_ReheatFunc | SNVT_count | Xzone reheat func | 0 | 1 |  | 0
539 | 1749 | nvoXZ_ReheatFunc | SNVT_count | Xzone reheat func
540 | 1752 | nviXZ_CoolFunc | SNVT_count | Xzone cool func | 0 | 1 |  | 0
541 | 1753 | nvoXZ_CoolFunc | SNVT_count | Xzone cool func
Xzone temperature regulation
542 | 1756 | nviXZ_Tempregmod | SNVT_count | Xzone tempregmode 1=ERS-1, 2=ERS-2, 3=SA, 4=EA, 5=ORS, 6=ORE | 1 | 6 |  | 1
543 | 1757 | nvoXZ_Tempregmod | SNVT_count | Xzone tempregmode
Xzone ERS-1 reg.
544 | 1760 | nviXZ_ERS1step | SNVT_count | Xzone ERS 1 Step Curve setting according to the diagram for ERS 1. | 1 | 4
545 | 1761 | nvoXZ_ERS1step | SNVT_count | Xzone ERS 1 Step
546 | 1762 | nviXZ_ERS1diff | SNVT_temp_p | Xzone SA temp diff set ERS 1 Supply air temp differental setting according to the diagram for ERS 1. | 1 | 7.00 | K | 2.00
547 | 1763 | nvoXZ_ERS1diff | SNVT_temp_p | Xzone SA temp diff set ERS 1
548 | 1764 | nviXZ_ERS1brkpnt | SNVT_temp_p | Xzone ERS 1 Brkpnt Breakpoint temp setting according to the diagram for ERS 1. | 12.00 | 26.00 | °C | 22.00
549 | 1765 | nvoXZ_ERS1brkpnt | SNVT_temp_p | Xzone ERS 1 Brkpnt
Xzone ERS-2 reg.
550 | 1770 | nviXZ_ERS2_X1 | SNVT_temp_p | Xzone ERS 2 Brkpnt_X1 Breakpoint X1 setting according to the diagram for ERS 2. | 10 | NV 553 | °C | 15.00
551 | 1771 | nvoXZ_ERS2_X1 | SNVT_temp_p | Xzone ERS 2 Brkpnt_X1
552 | 1772 | nviXZ_ERS2_X2 | SNVT_temp_p | Xzone ERS 2 Brkpnt_X2 Breakpoint X2 setting according to the diagram for ERS 2. | NV 551 | NV 555 | °C | 20.00
553 | 1773 | nvoXZ_ERS2_X2 | SNVT_temp_p | Xzone ERS 2 Brkpnt_X2
554 | 1774 | nviXZ_ERS2_X3 | SNVT_temp_p | Xzone ERS 2 Brkpnt_X3 Breakpoint X3 setting according to the diagram for ERS 2. | NV 553 | NV 557 | °C | 22.00
555 | 1775 | nvoXZ_ERS2_X3 | SNVT_temp_p | Xzone ERS 2 Brkpnt_X3
556 | 1776 | nviXZ_ERS2_X4 | SNVT_temp_p | Xzone ERS 2 Brkpnt_X4 Breakpoint X4 setting according to the diagram for ERS 2. | NV 555 | 40.00 | °C | 24.00
557 | 1777 | nvoXZ_ERS2_X4 | SNVT_temp_p | Xzone ERS 2 Brkpnt_X4
558 | 1778 | nviXZ_ERS2_Y1 | SNVT_temp_p | Xzone ERS 2 Brkpnt_Y1 Breakpoint Y1 setting according to the diagram for ERS 2. | 10.00 | 40.00 | °C | 20.00
559 | 1779 | nvoXZ_ERS2_Y1 | SNVT_temp_p | Xzone ERS 2 Brkpnt_Y1
560 | 1780 | nviXZ_ERS2_Y2 | SNVT_temp_p | Xzone ERS 2 Brkpnt_Y2 Breakpoint Y2 setting according to the diagram for ERS 2. | 10.00 | 40.00 | °C | 18.00
561 | 1781 | nvoXZ_ERS2_Y2 | SNVT_temp_p | Xzone ERS 2 Brkpnt_Y2
562 | 1782 | nviXZ_ERS2_Y3 | SNVT_temp_p | Xzone ERS 2 Brkpnt_Y3 Breakpoint Y3 setting according to the diagram for ERS 2. | 10.00 | 40.00 | °C | 14.00
563 | 1783 | nvoXZ_ERS2_Y3 | SNVT_temp_p | Xzone ERS 2 Brkpnt_Y3
564 | 1784 | nviXZ_ERS2_Y4 | SNVT_temp_p | Xzone ERS 2 Brkpnt_Y4 Breakpoint Y4 setting according to the diagram for ERS 2. | 10.00 | 40.00 | °C | 12.00
565 | 1785 | nvoXZ_ERS2_Y4 | SNVT_temp_p | Xzone ERS 2 Brkpnt_Y4
Xzone SA Reg.
566 | 1790 | nviXZ_SAtempset | SNVT_temp_p | Xzone SA temp Supply air temperature setting, for supply air temp regulation mode. | 10.00 | 40.00 | °C | 21.00
567 | 1791 | nvoXZ_SAtempset | SNVT_temp_p | Xzone SA temp
Xzone EA Reg.
568 | 1796 | nviXZ_EAtempset | SNVT_temp_p | Xzone EA temp Extract air/room temperature setting, for Extract air/room temp regulation mode. | 10.00 | 40.00 | °C | 21.00
569 | 1797 | nvoXZ_EAtempset | SNVT_temp_p | Xzone EA temp
570 | 1798 | nviXZ_MinSAtemp | SNVT_temp_p | Xzone SA Min temp Supply air min. set point during EA/room regulation mode. | 8.00 | 20.00 | °C | 16.00
571 | 1799 | nvoXZ_MinSAtemp | SNVT_temp_p | Xzone SA Min temp
572 | 1800 | nviXZ_MaxSAtemp | SNVT_temp_p | Xzone SA Max temp Supply air max. set point during EA/room regulation mode. | 16.00 | 50.00 | °C | 28.00
573 | 1801 | nvoXZ_MaxSAtemp | SNVT_temp_p | Xzone SA Max temp
574 | 1802 | nviXZ_EA_P-band | SNVT_temp_p | Xzone P-band | 1.00 | 10.00 | K | 5.00
575 | 1803 | nvoXZ_EA_P-band | SNVT_temp_p | Xzone P-band
576 | 1804 | nviXZ_EA_I-time | SNVT_time_sec | Xzone I-time | 1 | 1800 | s | 180
577 | 1805 | nvoXZ_EA_I-time | SNVT_time_sec | Xzone I-time
Xzone ORS Reg.
578 | 1806 | nviXZ_ORS_X1 | SNVT_temp_p | Xzone ORS Brkpnt_X1 Breakpoint X1 setting according to the diagram for ORS. | -5.00 | NV 581 | °C | -20.00
579 | 1807 | nvoXZ_ORS_X1 | SNVT_temp_p | Xzone ORS Brkpnt_X1
580 | 1808 | nviXZ_ORS_X2 | SNVT_temp_p | Xzone ORS Brkpnt_X2 Breakpoint X2 setting according to the diagram for ORS. | NV 579 | NV 583 | °C | -10.00
581 | 1809 | nvoXZ_ORS_X2 | SNVT_temp_p | Xzone ORS Brkpnt_X2
582 | 1810 | nviXZ_ORS_X3 | SNVT_temp_p | Xzone ORS Brkpnt_X3 Breakpoint X3 setting according to the diagram for ORS. | NV 581 | NV 585 | °C | 10.00
583 | 1811 | nvoXZ_ORS_X3 | SNVT_temp_p | Xzone ORS Brkpnt_X3
584 | 1812 | nviXZ_ORS_X4 | SNVT_temp_p | Xzone ORS Brkpnt_X4 Breakpoint X4 setting according to the diagram for ORS. | NV 583 | 50.00 | °C | 20.00
585 | 1813 | nvoXZ_ORS_X4 | SNVT_temp_p | Xzone ORS Brkpnt_X4
586 | 1814 | nviXZ_ORS_Y1 | SNVT_temp_p | Xzone ORS Brkpnt_Y1 Breakpoint Y1 setting according to the diagram for ORS. | 10.00 | 40.00 | °C | 21.50
587 | 1815 | nvoXZ_ORS_Y1 | SNVT_temp_p | Xzone ORS Brkpnt_Y1
588 | 1816 | nviXZ_ORS_Y2 | SNVT_temp_p | Xzone ORS Brkpnt_Y2 Breakpoint Y2 setting according to the diagram for ORS. | 10.00 | 40.00 | °C | 21.50
589 | 1817 | nvoXZ_ORS_Y2 | SNVT_temp_p | Xzone ORS Brkpnt_Y2
590 | 1818 | nviXZ_ORS_Y3 | SNVT_temp_p | Xzone ORS Brkpnt_Y3 Breakpoint Y3 setting according to the diagram for ORS. | 10.00 | 40.00 | °C | 21.50
591 | 1819 | nvoXZ_ORS_Y3 | SNVT_temp_p | Xzone ORS Brkpnt_Y3
592 | 1820 | nviXZ_ORS_Y4 | SNVT_temp_p | Xzone ORS Brkpnt_Y4 Breakpoint Y4 setting according to the diagram for ORS. | 10.00 | 40.00 | °C | 21.50
593 | 1821 | nvoXZ_ORS_Y4 | SNVT_temp_p | Xzone ORS Brkpnt_Y4
Xzone ORE Reg.
594 | 1826 | nviXZ_ORE_X1 | SNVT_temp_p | Xzone ORE Brkpnt_X1 Breakpoint X1 setting according to the diagram for ORE. | -5.00 | NV 597 | °C | -20.00
595 | 1827 | nvoXZ_ORE_X1 | SNVT_temp_p | Xzone ORE Brkpnt_X1
596 | 1828 | nviXZ_ORE_X2 | SNVT_temp_p | Xzone ORE Brkpnt_X2 Breakpoint X2 setting according to the diagram for ORE. | NV 595 | NV 599 | °C | -10.00
597 | 1829 | nvoXZ_ORE_X2 | SNVT_temp_p | Xzone ORE Brkpnt_X2
598 | 1830 | nviXZ_ORE_X3 | SNVT_temp_p | Xzone ORE Brkpnt_X3 Breakpoint X3 setting according to the diagram for ORE. | NV 597 | NV 601 | °C | 10.00
599 | 1831 | nvoXZ_ORE_X3 | SNVT_temp_p | Xzone ORE Brkpnt_X3
600 | 1832 | nviXZ_ORE_X4 | SNVT_temp_p | Xzone ORE Brkpnt_X4 Breakpoint X4 setting according to the diagram for ORE. | NV 599 | 50.00 | °C | 20.00
601 | 1833 | nvoXZ_ORE_X4 | SNVT_temp_p | Xzone ORE Brkpnt_X4
602 | 1834 | nviXZ_ORE_Y1 | SNVT_temp_p | Xzone ORE Brkpnt_Y1 Breakpoint Y1 setting according to the diagram for ORE. | 10.00 | 40.00 | °C | 21.50
603 | 1835 | nvoXZ_ORE_Y1 | SNVT_temp_p | Xzone ORE Brkpnt_Y1
604 | 1836 | nviXZ_ORE_Y2 | SNVT_temp_p | Xzone ORE Brkpnt_Y2 Breakpoint Y2 setting according to the diagram for ORE. | 10.00 | 40.00 | °C | 21.50
605 | 1837 | nvoXZ_ORE_Y2 | SNVT_temp_p | Xzone ORE Brkpnt_Y2
606 | 1838 | nviXZ_ORE_Y3 | SNVT_temp_p | Xzone ORE Brkpnt_Y3 Breakpoint Y3 setting according to the diagram for ORE. | 10.00 | 40.00 | °C | 21.50
607 | 1839 | nvoXZ_ORE_Y3 | SNVT_temp_p | Xzone ORE Brkpnt_Y3
608 | 1840 | nviXZ_ORE_Y4 | SNVT_temp_p | Xzone ORE Brkpnt_Y4 Breakpoint Y4 setting according to the diagram for ORE. | 10.00 | 40.00 | °C | 21.50
609 | 1841 | nvoXZ_ORE_Y4 | SNVT_temp_p | Xzone ORE Brkpnt_Y4
Xzone external sensors
610 | 1854 | nviXZ_RoomTempFu | SNVT_count | Xzone EA/Room temp ext func 0=Average, 1=Min, 2=Max | 0 | 2 |  | 0
611 | 1855 | nvoXZ_RoomTempFu | SNVT_count | Xzone EA/Room temp ext func
612 | 1856 | nviXZ_RoomBMSFu | SNVT_count | Xzone EA/Room temp from BMS func | 0 | 1 |  | 0
613 | 1857 | nvoXZ_RoomBMSFu | SNVT_count | Xzone EA/Room temp from BMS func
614 | 1858 | nviXZ_RoomTmpBMS | SNVT_temp_p | Xzone EA/Room temp from BMS | -55.00 | 125.00 | °C | 0.00
615 | 1859 | nvoXZ_RoomTmpBMS | SNVT_temp_p | Xzone EA/Room temp from BMS
616 | 1860 | nviXZ_RoomBMSAl | SNVT_time_min | Xzone EA/Room temp from BMS alarm | 0 | 9999 | min | 5
617 | 1861 | nvoXZ_RoomBMSAl | SNVT_time_min | Xzone EA/Room temp from BMS alarm
Xzone Heat/Cool
618 | 1866 | nviXZ_ReHeat_P-b | SNVT_temp_p | Xzone ReHeat P-band | 1.00 | 10.00 | K | 8.00
619 | 1867 | nvoXZ_ReHeat_P-b | SNVT_temp_p | Xzone ReHeat P-band
620 | 1868 | nviXZ_ReHeat_I-t | SNVT_time_sec | Xzone ReHeat I-time | 1 | 1800 | s | 70
621 | 1869 | nvoXZ_ReHeat_I-t | SNVT_time_sec | Xzone ReHeat I-time
622 | 1888 | nviXZ_Cool_reg_f | SNVT_count | Xzone Cool on/off regulation func 0=Inactive, 1=1 step, 2=2 steps, 3=3 steps. | 0 | 3 |  | 0
623 | 1889 | nvoXZ_Cool_reg_f | SNVT_count | Xzone Cool on/off regulation func
624 | 1890 | nviXZ_Cool_SA_NZ | SNVT_temp_p | Xzone Cool SA neutral zone | 0.50 | 10.00 | K | 2.00
625 | 1891 | nvoXZ_Cool_SA_NZ | SNVT_temp_p | Xzone Cool SA neutral zone
626 | 1892 | nviXZ_Cool_EA_NZ | SNVT_temp_p | Xzone Cool EA neutral zone | 0.50 | 10.00 | K | 2.00
627 | 1893 | nvoXZ_Cool_EA_NZ | SNVT_temp_p | Xzone Cool EA neutral zone
628 | 1894 | nviXZ_Cool_P-b | SNVT_temp_p | Xzone Cool P-band | 1.00 | 10.00 | K | 6.00
629 | 1895 | nvoXZ_Cool_P-b | SNVT_temp_p | Xzone Cool P-band
630 | 1896 | nviXZ_Cool_I-t | SNVT_time_sec | Xzone Cool I-time | 1 | 1800 | s | 60
631 | 1897 | nvoXZ_Cool_I-t | SNVT_time_sec | Xzone Cool I-time
Pre-heat
632 | 1918 | nviPreHeatFunc | SNVT_count | Preheating func | 0 | 1 |  | 0
633 | 1919 | nvoPreHeatFunc | SNVT_count | Preheating func
634 | 1920 | nviPreHeatTmpSet | SNVT_temp_p | Preheating temp set | -40.00 | 40.00 | °C | 5.00
635 | 1921 | nvoPreHeatTmpSet | SNVT_temp_p | Preheating temp set
636 | 1922 | nviPreHeat_P-b | SNVT_temp_p | Preheat P-band | 1.00 | 10.00 | K | 8.00
637 | 1923 | nvoPreHeat_P-b | SNVT_temp_p | Preheat P-band
638 | 1924 | nviPreHeat_I-t | SNVT_time_sec | Preheat I-time | 1 | 1800 | s | 70
639 | 1925 | nvoPreHeat_I-t | SNVT_time_sec | Preheat I-time
ReCO2
640 | 1944 | nviReCO2_CO2_fu | SNVT_count | ReCO2 CO2 func 0=Inactive, 1=CO2, 2=CO2 and air flow boost | 0 | 2 |  | 0
641 | 1945 | nvoReCO2_CO2_fu | SNVT_count | ReCO2 CO2 func
642 | 1946 | nviReCO2_Temp_fu | SNVT_count | ReCO2 temp func 0=Inactive, 1=Heat, 2=Cool, 3=Heat and Cool. | 0 | 3 |  | 0
643 | 1947 | nvoReCO2_Temp_fu | SNVT_count | ReCO2 temp func
644 | 1950 | nviReCO2_CO2_set | SNVT_lev_percent | ReCO2 CO2 set | 0.00 | 100.00 | % | 50.00
645 | 1951 | nvoReCO2_CO2_set | SNVT_lev_percent | ReCO2 CO2 set
646 | 1952 | nviReCO2_MinOutA | SNVT_flow | ReCO2 min outdoor air | 0 | NV 89 | l/s
647 | 1953 | nvoReCO2_MinOutA | SNVT_flow | ReCO2 min outdoor air
648 | 1954 | nviReCO2_MinExhA | SNVT_flow | ReCO2 min exhaust air | 0 | NV 90 | l/s
649 | 1955 | nvoReCO2_MinExhA | SNVT_flow | ReCO2 min exhaust air
650 | 1956 | nviReCO2_CO2_P-b | SNVT_lev_percent | ReCO2 CO2 P-band | 1.00 | 100.00 | % | 50.00
651 | 1957 | nvoReCO2_CO2_P-b | SNVT_lev_percent | ReCO2 CO2 P-band
652 | 1958 | nviReCO2_CO2_I-t | SNVT_time_sec | ReCO2 CO2 I-time | 1 | 1800 | s | 60
653 | 1959 | nvoReCO2_CO2_I-t | SNVT_time_sec | ReCO2 CO2 I-time
654 | 1960 | nviReCO2_CO2F_Pb | SNVT_lev_percent | ReCO2 CO2 flow P-band | 10.00 | 100.00 | % | 50.00
655 | 1961 | nvoReCO2_CO2F_Pb | SNVT_lev_percent | ReCO2 CO2 flow P-band
656 | 1962 | nviReCO2_CO2F_It | SNVT_time_sec | ReCO2 CO2 flow I-time | 1 | 1800 | s | 60
657 | 1963 | nvoReCO2_CO2F_It | SNVT_time_sec | ReCO2 CO2 flow I-time
658 | 1964 | nviReCO2_Heat_Pb | SNVT_lev_percent | ReCO2 heat P-band | 1.00 | 10.00 | K | 7.00
659 | 1965 | nvoReCO2_Heat_Pb | SNVT_lev_percent | ReCO2 heat P-band
660 | 1966 | nviReCO2_Heat_It | SNVT_time_sec | ReCO2 heat I-time | 1 | 1800 | s | 70
661 | 1967 | nvoReCO2_Heat_It | SNVT_time_sec | ReCO2 heat I-time
662 | 1968 | nviReCO2_Cool_Pb | SNVT_lev_percent | ReCO2 cool P-band | 1.00 | 10.00 | K | 6.00
663 | 1969 | nvoReCO2_Cool_Pb | SNVT_lev_percent | ReCO2 cool P-band
664 | 1970 | nviReCO2_Cool_It | SNVT_time_sec | ReCO2 cool I-time | 1 | 1800 | s | 60
665 | 1971 | nvoReCO2_Cool_It | SNVT_time_sec | ReCO2 cool I-time
Humidity/VOC
666 | 1980 | nviHumidi_func | SNVT_count | Humidi func 0=Inactive, 1=on/off, 2=0-10V | 0 | 2 |  | 0
667 | 1981 | nvoHumidi_func | SNVT_count | Humidi func
668 | 1984 | nviHumidi_start | SNVT_lev_percent | Humidi on/off start | 10.00 | NV 671 | %RH | 40.00
669 | 1985 | nvoHumidi_start | SNVT_lev_percent | Humidi on/off start
670 | 1986 | nviHumidi_stop | SNVT_lev_percent | Humidi on/off stop | NV 669 | 95.00 | %RH | 45.00
671 | 1988 | nvoHumidi_stop | SNVT_lev_percent | Humidi on/off stop
672 | 1994 | nviHum_0-10_Set | SNVT_lev_percent | Humidi 0-10V set | 10.00 | 95.00 | %RH | 30.00
673 | 1995 | nvoHum_0-10_Set | SNVT_lev_percent | Humidi 0-10V set
674 | 1996 | nviHum_0-10_Max | SNVT_lev_percent | Humidi 0-10V max | 10.00 | 95.00 | %RH | 80.00
675 | 1997 | nvoHum_0-10_Max | SNVT_lev_percent | Humidi 0-10V max
676 | 1998 | nviHum_0-10_SA_P | SNVT_lev_percent | Humidi 0-10V SA P-band | 1.00 | 80.00 | %RH | 60.00
677 | 1999 | nvoHum_0-10_SA_P | SNVT_lev_percent | Humidi 0-10V SA P-band
678 | 2000 | nviHum_0-10_SA_I | SNVT_time_sec | Humidi 0-10V SA I-time | 1 | 1800 | s | 30
679 | 2001 | nvoHum_0-10_SA_I | SNVT_time_sec | Humidi 0-10V SA I-time
680 | 1998 | nviHum_0-10_EA_P | SNVT_lev_percent | Humidi 0-10V EA P-band | 1.00 | 80.00 | %RH | 60.00
681 | 1999 | nvoHum_0-10_EA_P | SNVT_lev_percent | Humidi 0-10V EA P-band
682 | 2000 | nviHum_0-10_EA_I | SNVT_time_sec | Humidi 0-10V EA I-time | 1 | 1800 | s | 180
683 | 2001 | nvoHum_0-10_EA_I | SNVT_time_sec | Humidi 0-10V EA I-time
684 | 2014 | nviDehumidi_Set | SNVT_lev_percent | Dehumidi setpoint | 10.00 | 90.00 | %RH | 50.00
685 | 2015 | nvoDehumidi_Set | SNVT_lev_percent | Dehumidi setpoint
SMART Link
686 | 2062 | nviSL_WB_HeatSet | SNVT_temp_p | SL WB heat temp set | -40.0 | 176.0 | °C | 40.0
687 | 2063 | nvoSL_WB_HeatSet | SNVT_temp_p | SL WB heat temp set
688 | 2064 | nviSL_WB_HeatZon | SNVT_temp_p | SL WB heat temp zone | 1.0 | 10.0 | K | 3.0
689 | 2065 | nvoSL_WB_HeatZon | SNVT_temp_p | SL WB heat temp zone
690 | 2066 | nviSL_WB_CoolSet | SNVT_temp_p | SL WB cool temp set | -40.0 | 176.0 | °C | 12.0
691 | 2067 | nvoSL_WB_CoolSet | SNVT_temp_p | SL WB cool temp set
692 | 2068 | nviSL_WB_CoolZon | SNVT_temp_p | SL WB cool temp zone | 1.0 | 10.0 | K | 2.0
693 | 2069 | nvoSL_WB_CoolZon | SNVT_temp_p | SL WB cool temp zone
694 | 2080 | nviSL_WB_Op_V_Up | SNVT_lev_percent | SL WB op valve upper | 5.0 | 90.0 | % | 80.0
695 | 2081 | nvoSL_WB_Op_V_Up | SNVT_lev_percent | SL WB op valve upper
696 | 2082 | nviSL_WB_Op_V_Lo | SNVT_lev_percent | SL WB op valve lower | 70.0 | 100.0 | % | 100.0
697 | 2083 | nvoSL_WB_Op_V_Lo | SNVT_lev_percent | SL WB op valve lower
698 | 2084 | nviSL_WB_OpDelay | SNVT_time_sec | SL WB op time delay | 30 | 32000 | s | 60
699 | 2085 | nvoSL_WB_OpDelay | SNVT_time_sec | SL WB op time delay
700 | 2128 | nviSL_DX_DeDelay | SNVT_time_sec | SL DX defrost time delay | 30 | 900 | s | 90
701 | 2129 | nvoSL_DX_DeDelay | SNVT_time_sec | SL DX defrost time delay
AYC
702 | 2146 | nviAYCHeatTmpSet | SNVT_temp_p | AYC heat temp set | 10.00 | 80.00 | °C | 30.00
703 | 2147 | nvoAYCHeatTmpSet | SNVT_temp_p | AYC heat temp set
704 | 2172 | nviAYCHeatOutCX1 | SNVT_temp_p | AYC heat out cmp X1 | -40.00 | NV 707 | °C | -20.00
705 | 2173 | nvoAYCHeatOutCX1 | SNVT_temp_p | AYC heat out cmp X1
706 | 2174 | nviAYCHeatOutCX2 | SNVT_temp_p | AYC heat out cmp X2 | NV 705 | NV 709 | °C | 0.00
707 | 2175 | nvoAYCHeatOutCX2 | SNVT_temp_p | AYC heat out cmp X2
708 | 2176 | nviAYCHeatOutCX3 | SNVT_temp_p | AYC heat out cmp X3 | NV 707 | NV 711 | °C | 5.00
709 | 2177 | nvoAYCHeatOutCX3 | SNVT_temp_p | AYC heat out cmp X3
710 | 2178 | nviAYCHeatOutCX4 | SNVT_temp_p | AYC heat out cmp X4 | NV 709 | 40.00 | °C | 15.00
711 | 2179 | nvoAYCHeatOutCX4 | SNVT_temp_p | AYC heat out cmp X4
712 | 2180 | nviAYCHeatOutCY1 | SNVT_temp_p | AYC heat out cmp Y1 | -40.00 | 40.00 | °C | 40.00
713 | 2181 | nvoAYCHeatOutCY1 | SNVT_temp_p | AYC heat out cmp Y1
714 | 2182 | nviAYCHeatOutCY2 | SNVT_temp_p | AYC heat out cmp Y2 | -40.00 | 40.00 | °C | 30.00
715 | 2183 | nvoAYCHeatOutCY2 | SNVT_temp_p | AYC heat out cmp Y2
716 | 2184 | nviAYCHeatOutCY3 | SNVT_temp_p | AYC heat out cmp Y3 | -40.00 | 40.00 | °C | 20.00
717 | 2185 | nvoAYCHeatOutCY3 | SNVT_temp_p | AYC heat out cmp Y3
718 | 2186 | nviAYCHeatOutCY4 | SNVT_temp_p | AYC heat out cmp Y4 | -40.00 | 40.00 | °C | 15.00
719 | 2187 | nvoAYCHeatOutCY4 | SNVT_temp_p | AYC heat out cmp Y4
720 | 2196 | nviAYCHeatRoomCp | SNVT_temp_p | AYC heat room cmp tmp | 0.00 | 40.00 | °C | 21.00
721 | 2197 | nvoAYCHeatRoomCp | SNVT_temp_p | AYC heat room cmp tmp
722 | 2198 | nviAYCHeatRoomPb | SNVT_temp_p | AYC heat room cmp P-band | 1.00 | 10.00 | K | 5.00
723 | 2199 | nvoAYCHeatRoomPb | SNVT_temp_p | AYC heat room cmp P-band
724 | 2206 | nviAYCHeatNghtCp | SNVT_temp_p | AYC heat night cmp tmp | -10.00 | 10.00 | K | -2.00
725 | 2207 | nvoAYCHeatNghtCp | SNVT_temp_p | AYC heat night cmp tmp
726 | 2236 | nviAYC_Heat_P-b | SNVT_temp_p | AYC heat P-band | 1.00 | 40..00 | K | 15.00
727 | 2237 | nvoAYC_Heat_P-b | SNVT_temp_p | AYC heat P-band
728 | 2238 | nviAYC_Heat_I-t | SNVT_time_sec | AYC heat I-time | 1 | 600 | s | 60
729 | 2239 | nvoAYC_Heat_I-t | SNVT_time_sec | AYC heat I-time
730 | 2242 | nviAYCCoolTmpSet | SNVT_temp_p | AYC cool temp set | 10.00 | 80.00 | °C | 30.00
731 | 2243 | nvoAYCCoolTmpSet | SNVT_temp_p | AYC cool temp set
732 | 2270 | nviAYCCoolOutCX1 | SNVT_temp_p | AYC cool out cmp X1 | -40.00 | NV 735 | °C | -20.00
733 | 2271 | nvoAYCCoolOutCX1 | SNVT_temp_p | AYC cool out cmp X1
734 | 2272 | nviAYCCoolOutCX2 | SNVT_temp_p | AYC cool out cmp X2 | NV 733 | NV 737 | °C | 0.00
735 | 2273 | nvoAYCCoolOutCX2 | SNVT_temp_p | AYC cool out cmp X2
736 | 2274 | nviAYCCoolOutCX3 | SNVT_temp_p | AYC cool out cmp X3 | NV 735 | NV 739 | °C | 5.00
737 | 2275 | nvoAYCCoolOutCX3 | SNVT_temp_p | AYC cool out cmp X3
738 | 2276 | nviAYCCoolOutCX4 | SNVT_temp_p | AYC cool out cmp X4 | NV 737 | 40.00 | °C | 15.00
739 | 2277 | nvoAYCCoolOutCX4 | SNVT_temp_p | AYC cool out cmp X4
740 | 2278 | nviAYCCoolOutCY1 | SNVT_temp_p | AYC cool out cmp Y1 | -40.00 | 40.00 | °C | 40.00
741 | 2279 | nvoAYCCoolOutCY1 | SNVT_temp_p | AYC cool out cmp Y1
742 | 2280 | nviAYCCoolOutCY2 | SNVT_temp_p | AYC cool out cmp Y2 | -40.00 | 40.00 | °C | 30.00
743 | 2281 | nvoAYCCoolOutCY2 | SNVT_temp_p | AYC cool out cmp Y2
744 | 2282 | nviAYCCoolOutCY3 | SNVT_temp_p | AYC cool out cmp Y3 | -40.00 | 40.00 | °C | 20.00
745 | 2283 | nvoAYCCoolOutCY3 | SNVT_temp_p | AYC cool out cmp Y3
746 | 2284 | nviAYCCoolOutCY4 | SNVT_temp_p | AYC cool out cmp Y4 | -40.00 | 40.00 | °C | 15.00
747 | 2285 | nvoAYCCoolOutCY4 | SNVT_temp_p | AYC cool out cmp Y4
748 | 2294 | nviAYCCoolRoomCp | SNVT_temp_p | AYC cool room cmp tmp | 0.00 | 40.00 | °C | 21.00
749 | 2295 | nvoAYCCoolRoomCp | SNVT_temp_p | AYC cool room cmp tmp
750 | 2296 | nviAYCCoolRoomPb | SNVT_temp_p | AYC cool room cmp P-band | 1.00 | 10.00 | K | 5.00
751 | 2297 | nvoAYCCoolRoomPb | SNVT_temp_p | AYC cool room cmp P-band
752 | 2304 | nviAYCCoolNghtCp | SNVT_temp_p | AYC cool night cmp tmp | -10.00 | 10.00 | K | -2.00
753 | 2305 | nvoAYCCoolNghtCp | SNVT_temp_p | AYC cool night cmp tmp
754 | 2336 | nviAYCCoolDewCpZ | SNVT_temp_p | AYC cool dew point cmp zone | 0 | 5.00 | K | 2.00
755 | 2337 | nvoAYCCoolDewCpZ | SNVT_temp_p | AYC cool dew point cmp zone
756 | 2338 | nviAYCCoolDewCpS | SNVT_lev_percent | AYC cool dew point cmp speed Percent air flow boost of each increased chilled water set point. | 0 | 30.00 | %/K | 10.00
757 | 2339 | nvoAYCCoolDewCpS | SNVT_lev_percent | AYC cool dew point cmp speed
758 | 2344 | nviAYC_Cool_P-b | SNVT_temp_p | AYC cool P-band | 1.00 | 40..00 | K | 15.00
759 | 2345 | nvoAYC_Cool_P-b | SNVT_temp_p | AYC cool P-band
760 | 2346 | nviAYC_Cool_I-t | SNVT_time_sec | AYC cool I-time | 1 | 600 | s | 60
761 | 2347 | nvoAYC_Cool_I-t | SNVT_time_sec | AYC cool I-time
Optimize
762 | 2372 | nviOptimize_func | SNVT_count | Optimize func | 0 | 1 |  | 0
763 | 2373 | nvoOptimize_func | SNVT_count | Optimize func
764 | 2374 | nviOptimizeSAset | SNVT_press_p | Optimize SA press set | 20.0 | 750.0 | Pa | 0
765 | 2375 | nvoOptimizeSAset | SNVT_press_p | Optimize SA press set
766 | 2376 | nviOptimizeEAset | SNVT_press_p | Optimize EA press set | 20.0 | 750.0 | Pa | 0
767 | 2377 | nvoOptimizeEAset | SNVT_press_p | Optimize EA press set
Operation level settings
768 | 2684 | nviComOperation | SNVT_count | Com operation mode 0=auto, 1=total stop, 2=low speed, 3=high speed, 4=normal stop, 5=extended normal stop. | 0 | 5 |  | 0
769 | 2685 | nvoComOperation | SNVT_count | Com operation mode
770 | 4000 | nviComOp_Auto | SNVT_switch | Auto Op | 0 | 1 |  | 0
771 | 4001 | nvoComOp_Auto | SNVT_switch | Auto Op
772 | 4002 | nviComOp_T_Stop | SNVT_switch | Com total stop | 0 | 1 |  | 0
773 | 4003 | nvoComOp_T_Stop | SNVT_switch | Com total stop
774 | 4004 | nviComOp_LS | SNVT_switch | Com LS | 0 | 1 |  | 0
775 | 4005 | nvoComOp_LS | SNVT_switch | Com LS
776 | 4006 | nviComOp_HS | SNVT_switch | Com HS | 0 | 1 |  | 0
777 | 4007 | nvoComOp_HS | SNVT_switch | Com HS
778 | 4008 | nviComOp_N_Stop | SNVT_switch | Com normal stop | 0 | 1 |  | 0
779 | 4009 | nvoComOp_N_Stop | SNVT_switch | Com normal stop
780 | 4010 | nviComOp_E_Stop | SNVT_switch | Com extended stop | 0 | 1 |  | 0
781 | 4011 | nvoComOp_E_Stop | SNVT_switch | Com extended stop
Time schedule
782 | 2930 | nviClock | SNVT_time_stamp | Clock Setting for the unit's internal clock
783 | 2931 | nvoClock | SNVT_time_stamp | Clock
784 | 2962 | nviTS_DefaultAct | SNVT_count | Time schedule default action 1=Total stop, 2=Low speed, 3=High speed, 4=Normal stop, 5=Extended normal stop | 1 | 5 |  | 2
785 | 2963 | nvoTS_DefaultAct | SNVT_count | Time schedule default action
Internal
786 | 5000 | nvoMajorVerLon | SNVT_count | Major version of SW in GW Major version of software in LonWorks gateway.
787 | 5001 | nvoMinorVerLon | SNVT_count | Minor version of SW in GW Minor version of software in LonWorks gateway.
788 | 1 | nvoObjStatus | SNVT_obj_status | Response status variable to obj_request
789 | 2 | nviObjRequest | SNVT_obj_request | Request variable for status of obj_status
790 |  | nciAutoSendTime | SNVT_time_sec | Autoupdate of all netvars This variable defines the time it takes for all the parameters to be automatically updated on the network. 0 = The Autosend function is disabled.
791 |  | nciSndHrtBt | SNVT_time_sec | Send Heartbeat Time 0 = The send heartbeat function is disabled.
792 |  | nciRcvHrtBt | SNVT_time_sec | Receive Heartbeat Time 0 = The receive heartbeat function is disabled.
793 |  | nciMinOutTm | SNVT_time_sec | Min Time Between updates Minimum period of time between automatic network variable output transmissons. 0 = The min time between function is disabled.
794 |  | nciLocation | SNVT_str_asc | Location
795 |  | nciSwitchCfg | SNVT_count | SNVT_switch inp 0=as spec,>=1 value OR state